## QMP
|  | Inspection and Testing Plan for Building and General Infrastructures (Civil and Mechanical Items) | [7 empty] | Doc. No :TAPF/QMS/PE/CAPEX/SOP-07 Rev : 0 Date : 28-04-2022
Sr. No. | Type of Marerial | Parameters | Relevant code or standerd | Norms | Frequency of Test | Sampling Point | Action when Non- Confirming | Report/Test Require | Responsibility |  |  | If Not satisfied with Reports
[9 empty] | Contractor | PMC | Client
1 | OPC Cement (IS 12269) | Chemical Test. | [6 empty] | P | W | R | External Lab
|  | 1) Insoluble Residue (% by Mass | ASTM C114 - 11b (1999) | 2% Maxi. | Every LOT/ Up to 100 bags/ As required | Plant/Site | Change cement source / Return to vendor | MTC/Test Report
|  | 2) Mananesia (% by Mass) | ASTM C114 - 11b L1999) | 6% Maxi.
|  | 3) Sulphuric anhydnde (% by mass) | ASTM C114 - 11b (1999) | 3% Maxi,
|  | 4)Total Loss of Ignition(%) | ASTM C114 - 11b (1999) | 5% Maxi
|  | 5) Chloride(%) | ASTM C114 - 11b (1999) | 0.05 Maxi.
|  | 6) % Lime to Silica | ASTM C114 - 11 b (1999) | 0 8-1 02
|  | 7) % Alumina to Iron oxide | ASTM C114 - 11 b (1999) | 0.66 mini.
|  | Physical Test: | [6 empty] | P | W | R | External Lab
|  | 1) Standard Cons stency | IS 12269 (2013) & IS 4031- Part 4 (2009) |  | Every LOT/ Up to 100 bags/ As required | Plant/Site | Change cement source / Return to vendor | MTC/Test Report
|  | 2) Initial setting Time | IS 12269 (2013) & IS 4031- Part 4 (2009) | 300 min. Mini.
|  | 3) Final Setting Time | IS 12269 (2013) & IS 4031- Part 4 (2009) | 600 Min Maxi
4) Compressive Strength
|  | a. 72+/- 1 Hour | IS 12269 (2013) & IS 4031- Part 6 (2009) | 27 N/mm²
|  | b. 168 +/- 2 Hours | IS 12269 (2013) & IS 4031- Part 6 (2009) | 37 N/mm²
|  | c. 672 +/- 4 Hours | IS 12269 (2013) & IS 4031- Part 6 (2009) | 53 N/mm²
|  | S) Fineness m² /Kq | IS 12269 (2013) & IS 4031- Part 4 (2009) | 225 Mini.
|  | 6) Soundness by Le-chat | IS 12269 (2013) & IS 4031- Part 4 (2009) | 10 mm Maxi.
2 | HYSD (TMT) Bars Fe 500 or 500D | Chemical Test: | [6 empty] | P | W | R | External Lab
|  | 1) Carbon | IS 1786 (2008) | 0.25% Max. | Each LOT/ Upto 50 MT - 1 Test | Source/Site | Return to vendor | MTC/TDS /Test Report
|  | 2) Suioher | IS 1786 (2008) | 0.04% Max.
|  | 3) Phosohorous | IS 1786 (2008) | 0 04 % Max
|  | 4) Sulpher and Phosphorus (Combined) | IS 1786 (2008) | 0.075 % Max.
|  | Physical Test: | [9 empty] | External Lab
|  | 1) 0.2 % Proof Stress | IS 1786 (2008), IS 1608 (2005) | 500 N/mm² | Each LOT/ Upto 50 MT - 1 Test | Source/Site | Return to vendor | MTC/TDS /Test Report
|  | 2) Ultimate Tensile Stress | IS 1786 (2008), IS 1608 (2005) | 565 N/mm²
|  | 3) Elongation | ¦S 1786 (2008), IS 1608 (2005) | 14.50 or 16 % Mini. For the Respective grades
|  | 4) Bend Test | IS 1786 (2008) IS 1608 (2005) | No Cracks
|  | 5) Nominal Mass | IS 1786 (2008) IS 1608 (2005) | Tab. 2 of IS 1786
3 | Coarse | 1) Specific Gravity | IS 2386-Part 3 (1963, 1997) | 2.6 Mini | once per source | Site | Return to vendor or use after regradation or for other enabling works. | Test Report | P | W | R | External Lab
2) DLBD
|  | 3) Water absorption | IS 2386-Part 3 (1963, 1997) | 2.0% Maxi. | Once in a Month/As Required
|  | 4) Aggregate impact value | IS 2386-Part 4 (1963, 1997) | 45 % Maxi | Once per source/ As require
|  | 5) Flakiness index | IS 2386-Part 1 (1963, 1997) | 35% Maximum | Once in a Month/As Required
|  | 6) Sieve Analysis | IS 383 (1970 1997) | T-2 of IS 383/Mix design | Every Lot
7) Moisture Content
4 | Fine Aggregate/Sand | 1) Sieve analysis & Fitness Modules | IS 383 (1970,1997) | Mix Design | Every Lot | site | Use after | Test Reports | P | W | R | External Lab
|  | 2) Moisture Content |  |  |  |  | Adjust W/C Ratio
|  | 3)Specific Gravity | IS 2386- Part-3 (l963,1997) | 2.6 mini. | Once per Source |  | Change source
|  | 4) Water absorption | IS 2386-Part 3 (1963,1997) | 2 % Maxi. | Once in a Month
|  | 5) Silt Content by Volume | IS 2386-Part 2 (1963,1998) | 8.5% Maxi. | Every LOT |  | Reuse after washing
|  | 6) Chlorides | IS 2386-Part 2 (1963,1998) | 500 mg/l maxi. | Once per Source |  | Change source
|  | 7) Sulphates | IS 2386-Part 2 (1963,1998) | 400 mg/l maxi.
5 | Water | 1) pH | IS 3025 (1964,2005) | Not less than 6 | Quarterly/Mansoon change /As Require | Source at site | Retest/Change the source | Test Report | Responsibility |  |  | External Lab
|  | 2) Organic Impurities | IS 3025 (1964,2005) | 200 mg/l Maxi. |  |  |  |  | P | W | R
|  | 3) Inorganic Impurities | 1S 3025 (1964,2005) | 300 mg/l Maxi.
|  | 4) Sulphates | IS 3025 (1964,2005) | 400 mg/l Maxi.
|  | 5) chloride (%) | IS 3025 (1964,2005) | 500 mg/l Maxi. For RCC and 2000 mg/l for PCC
|  | 6) Suspended Particles | IS 3025 (1964,2005) | 2000 mg/I Maxi
|  | 7) Hardness | IS 3025 (1964,2005) | Max. 300 mg/l
|  | 8) Turbidity | IS 3025 (1964,2005) | Max. 5 NTU
6 | Bentonite | 1) pH | IS 2911 Annex D (2010) | 9-10.5 | Every Batch | site | Retes/ Return to vendor | MTC/ Test Report | P | W | R | External Lab
|  | 2) Liquid Limit | IS 2911 Annex D (2010) | 400% mini.
|  | 3) Viscosity | IS 2911 Annex D (2010) | 30-60 sec
|  | 4) Density | IS 2911 Annex D (2010) | 1.03-1.10 g/ml
7 | ConcreteAdmixture | 1) pH | IS 9103 (1999) | 7 to 8 | Every Batch | Site | Retest/ Return to vender | MTC/Test Report | P | W | R | Manufacturer's Lab /External Lab
|  | 2) Sp. Gravity | IS 9103 (1999) | 0.2(+/-) of declared value
|  | 3) Dry material content | IS 9103 (1999) | Within 3% of MTC
|  | 4) Ash Content | IS 9103 (1999) | Within 1% of value of MTC
|  | 5) Chlorides ion Content | IS 9103 (1999) | With n 10 % of value of MTC or 0 2% which ever is greater
8 | Concrete | 1) Slump Test | IS 456 (2000) & IS 1199 (1959,1999) | 100-150mm for R/wall, 80-120mm for Raft Anchor slab, 50-100 for C C Block & PCC | one at pouring point | Pouring Point | Wait (When slump is more) & Redose up to required limit (when slump is less) up to required slump. Or use in enabling works. | Test Reports | P | W | R | Re-perform
2) Compressive strength test
|  | a. 7 days | IS 516 (1959,1999), IS 456 (2000), IS 1199 (1959,1999) | As per table No. 1of Gen Speci Section IV of MoRTH | Table 02 of IS 456 | Pouring Point | Acceptance Criteria / Non-Destructive Test / Destructive test. | Test Reports |  |  |  | External Lab
|  | b. 28 days | IS 516 (1959,1999), IS 456 (2000), IS 1199 (1959,1999)
|  | 3) Flexural Test | IS 516 (1959,1999), IS 456 (2000), IS 1199 (1959,1999) | 1. Mean strength for any group of 4 Consecutive test result exceed the specified characteristic Strength by at least 0.3 Mpa. 2. The strength determined from any resu]t is not less than the specified Characteristic strength less 3 mpa | AS recquire | Batching Plant/ Pouring Point | Acceptance Criteria | Test Reports |  |  |  | External Lab
9 | Soil | 1) Sieve Analysis | IS 2720-Part 4 (1985,1995) | 100 % Passing on 75 mm | Once per Source | Site | Reesorch or change the Source | Test Report | P | W | R | External Lab/ Site Lab
|  | 2) cohesion Coefficient © | IS 272a-Part 13 (1986) | 0 | Once per Source
|  | 3) Angle of internal Friction (fy) | IS 2720-Part 13 (1986) | Mini. 30 Degree | Once per Source | [6 empty] | External Lab
|  | 4) MDD/OMC | IS 2720-Part 7 & 8 (1980,1997) | Mini. 1.75 g/cc | Once for every change of Source | [6 empty] | External Lab/ Site Lab
|  | 5)Field Densiy/MoistureContent | IS 2720-Part28(1974,1995) | 95 % of MDD & +1/-2 of OMC | As Per scope/Location |  | Compaction & retest |  |  |  |  | Site
|  | 6) Relative Density | IS 2720-Part 14(1983,1995) | Max & Min Density | Once for every change of Source |  | Reesorch or change the Source |  |  |  |  | External Lab/ Site Lab
|  | 7) Densitv Index | IS 2720-Part 14 (1983,1995) | Mini 0.7 | 1 test per 1000 Sqm. |  | Compaction & Retest |  |  |  |  | External Lab
10 | Caibraion of Batching plant | 1) Aggregates | IS 4926 (2003) | Specification as per IS 4926 | Every 3 months | Site | Re-calibration / Repair | Test Report | P | W | R | Site Plant/ External Plant
|  | 2) Cement and water | IS 4926 (2003) | Specification as per IS 4926 | Every 3 months
|  | 3) Admixture | IS 4926 (2003) | Specification as per IS 4926 | Every 3 months
11 | Rcc NP-2/3/4 Hume pipe | 1) 3 edge bearing Test | IS 458 (2003) | as per IS 458 Table no. 3 | Every Lot | Factory | Resampling/ Retesting/ Change the Lot | Test Report | Responsibility |  |  | External Lab
|  | 2) Physical (Dimension) | IS 458 (2003) | as per IS 458 Cl. 7.2 |  |  |  |  | P | W | R
|  | 3) Hydrostatic Test | IS 458 (2003)& IS 3597 (1998,2003) | as per IS 3597 cl. 7.2.6
12 | CI Pipes | 1) Physical Testing for Tensile Strength | IS 1536 (2001), 1537 (1993), IS 7181 (1986) | Specification as per IS 1536, 1537, 7181 | Every Lot | Factory | Resampling/ Retesting/ Change the Lot | Test Report | P | W | R | External Lab
|  | 2) Hydrostatic Test | IS 1536 (2001), 1537 (1993), IS 7181 (1986) | Specification as per IS 1536, 1537, 7181
|  | 3) Physical Parameters Checking (Dimensions, Appearance, Ovality) | IS 1536 (2001), 1537 (1993), IS 7181 (1986) | Specification as per IS 1536, 1537, 7181
|  | 4) Test for Coating | IS 1536 (2001), 1537 (1993), IS7181 (1986) | Specification as per IS 1536,1537, 7181
13 | PVC Water Stopper | 1) Dimension | As per Tender Specs. | As per Tender Specs. | Every Lot | Factory/Site | Resampling/ Retesting/ Change the Lot | MTC/Test Report | P | W | R | External Lab
2) Visual Apperance
3) Tensile Strength
4) Ultimatde elongtion
5) Tear Resistence
6) Stiffness in Flexure
7) Accelerated Extraction
a. Tensile Strength
b. Ultimate elongation
8) Effect of alkali
9) Cold bend Test
14 | Bricks | 1) Dimension | IS 3495 (1992), 1077 (1992) | As per IS 3495 & 1077 | Every 50000 bricks or when the class of brick, type of brick and the source of brick are changed/physical Each lot | Site | Resampling/ Retesting/ Change the Lot | Test Report/ Third party | P | W | R | External Lab
2) Water Absorption
3) Compressive Strength
4) Efflorescence
16 | Glaze tiles/ Vitrified/ Mosaic titles/ Chequered titles/Terrazo | 1) Flexture Strength | IS 777(1988), IS 1237 (1980), 13630 (2006), 15622(2006) and as per tender spesification | As per IS 777(1988),IS 1237 (1980), 13630 (2006), 15622(2006) and tender specification | 1 Test per LOT | Site | Resampling/ Retesting/ Change the Lot | MTC | P | W | R | External Lab
2) Specific Gravity
3) Water Absorption
4) Absorption Resistence
17 | Kota Stone/ Granite | 1) Flexture Strength | IS 1121, 1122, 1124 (1974), 1123(1975) | As per IS 1121, 1122, 1124 (1974), 1123(1975) | 1 Test per LOT | Site | Resampling/ Retesting/ Change the Lot | Test Report | P | W | R | External Lab
2) Specific Gravity
3) Water Absorption
4) Absorption Resistence
18 | PVC Sheet | Physical and Chemical Perameters | IS 3462 (1986) and IS 3461 (1980) | As per IS 3462 (1986) and IS 3461(1980) | Every Lot | Site | Resampling/ Retesting/ Change the Lot | MTC | P | W | R | External Lab
19 | MS Structural Steel | Physical /Mechenical /Chemical Test | IS 2062,1161, 1239, 4923 | As per relevent Code | Every LOT | Site | Resampling/ Retesting/ Change the Lot | MTC | P | W | R | External Lab
20 | Wooden Work_ Wooden Frame (Timber) | Physical Parameters | IS 4021(1995), IS 287 (1993,1998), IS 710 (2010) | As per relevent Code | Every Lot | Site | Resampling/ Retesting/ Change the Lot | MTC/Test Report | P | W | R | External Lab
21 | Wooden Work _Flush Door shutter | Physical Parameters | IS 2202 Part I (1999) & Part- II (1983) | As per relevent Code | Every Lot | Site | Resampling/ Retesting/ Change the Lot | Test Report | P | W | R | External Lab
22 | Wooden Work_Transperent glass,Wired & figured glass | Physical Parameters | IS 2835(1983), IS 5437(1994) | As per relevent Code | As per tender spesification/Relevent Code |  | Return to vendor or use after | MTC/Test Report | P | W | R | External Lab
23 | Steel Doors and Windows | Physical Parameters | IS 7452(1990),IS 5437(1994), IS 1038(1983-1996), IS 1361 (1978,2001), IS 4351(2003), IS 6248(1979) | As per relevent Code | As per tender spesification/Relevent Code |  | Resampling/ Retesting/ Change the Lot | MTC/Test Report | P | W | R | External Lab
24 | Filler and Joint Sealing Compound | Physical and ChemicalParameters | IS 1838 Part-I (1983), IS 702(1988,1993), IS 3384(1986) | As per relevent Code | As per tender spesification/Relevent Code |  | Resampling/ Retesting/ Change the Lot | MTC/Test Report | P | W | R | External Lab
25 | Aluminium Doors, Windows,Ventilators & Partitions | Physical Parameter | IS:733 (1983), IS 1948(1961), IS 1949(1961) | As per Relevent Code | As per tender spesification/Relevent Code | site | Resampling/ Retesiing Change tbe Lot | MTC | Responsibility
[9 empty] | P | W | R | External Lab
26 | Painting for Concrete, Masonary and Plastered surface | Physical and Chemical Parameter | IS:428(2000), IS:5410(1992), IS:5411, IS:9862 (1981), IS:712 (1984), IS:2395 (1994) | As per Relevent Code | As per tender spesification/Relevent Code | site | Resampling/ Retesiing Change tbe Lot | MTC | P | R | R | External Lab
27 | Acrylic Paint | Physical and Chemical Parameter |  | As per Relevent Code | As per tender spesification/Relevent Code | site | Resampling/ Retesiing Change tbe Lot | MTC | P | R | R | External Lab
28 | Painting & Polishing of Wood Work | Physical and Chemical Parameter | IS: 3536(1999), IS:110, IS:337(1975),IS:340, IS:2932(2003) | As per Relevent Code | As per tender spesification/Relevent Code | site | Resampling/ Retesiing Change tbe Lot | MTC | P | R | R | External Lab
29 | Painting of Steel Work | Physical and Chemical Parameter | IS:2074(1992), IS:2932(2003), IS:2339 (1963), IS:1477 (pa rt-2) (1971, (1995) | As per Relevent Code | As per tender spesification/Relevent Code | site | Resampling/ Retesiing Change tbe Lot | MTC | P | R | R | External Lab
30 | PVC Pipe | Physical and Chemical Parameter | IS 4984-(1995), IS: 4985-1988(2000) | As per Relevent Code | As per tender spesification/Relevent Code | site | Resampling/ Retesiing Change tbe Lot | MTC | P | W | R | External Lab
31 | GI Pipe | Physical and Chemical Parameter | IS: 1239 Part-1 (2004) | As per Relevent Code | As per tender spesification/Relevent Code | site | Resampling/ Retesiing Change tbe Lot | MTC | P | W | R | External Lab
32 | Glazzed Stoneware Pipes | Physical and Chemical Parameter | IS: 651(2007), IS:4127(1983) | As per Relevent Code | As per tender spesification/Relevent Code | site | Resampling/ Retesiing Change tbe Lot | MTC | P | W | R | External Lab
33 | Taps | Physical Parameter | IS: 781(1984) | As per Relevent Code | As per tender spesification/Relevent Code | site | Resampling/ Retesiing Change tbe Lot | MTC | P | R | R | External Lab
34 | Sanitary Ware | Physical Parameter | IS:2556 (partIV), IS:1795(1982), IS:651(2007), IS:2556 (Part III) (2004) | As per Relevent Code | As per tender spesification/Relevent Code | site | Resampling/ Retesiing Change tbe Lot | MTC | P | R | R | External Lab
35 | Cast iron Gullies | Physical Parameter | IS:3989(1984) | As per Relevent Code | As per tender spesification/Relevent Code | site | Resampling/ Retesiing Change tbe Lot | MTC | P | R | R | External Lab
36 | Welding | Physical and Chemical Parameter | IS: 817(1966), IS:7310(part 1)(1974) and IS:7318(part 1)(1974),IS 7215(1974) | As per Relevent Code | As per tender spesification/Relevent Code | site | Resampiing/ Reascng Change ee Lai | Test Report | P | W | R | External Lab
37 | Sluice Valve | Physical Parameter | IS 1446(2000) and As per Tender Specifications | As per Relevent Code | As per tender spesification/Relevent Code | site | Resampling/ Retesiing Change tbe Lot | MTC | P | W | R | External Lab
Legends: P- Perform, W- Witness, R- Review, H- Holdpoint
Note :- 1) The tests not specified in the specification to check whether any work has defect or not, the same shall be conducted and submitted. 2) The test to be conducted as and when required by client/consultant (in-house and externally) shell be carried out at contractor's cost. 3) If necessary further item can be added/deleted later on for quality Assurance of the work. Any of the equipments contractor's site lab shall be calibrated in our witness.
SIGN & STAMP - CONTRACTOR |  |  |  | SIGN & STAMP - PMC |  |  |  | SIGN & STAMP - CLIENT