HEGDE AND HEGDE


THE AKSHAYA PATRA FOUNDATION
#72, 3RD FLOOR, 3RD MAIN ROAD, 1ST & 2ND STAGE, YESHWANTPUR INDUSTRIAL SUBURB, 

RAJAJINAGAR WARD NO. 10,
BENGALURU
CIVIL WORK


FOR

CONSTRUCTION OF ‘35K KITCHEN FACILITY’ 

AT AVALAHALLI, K.R.PURAM, 
BENGALURU.
[image: image9.png]



SECTION-II: GENERAL SPECIFICATIONS.

Scope of Specifications:

This specification gives general description of the works to be executed and a detailed description of materials and workmanship to be used therein. The specification shall be read in conjunction with the other forming part of the work included in the Contract.

Standard Specifications:

Unless specifically mentioned otherwise all relevant codes and standards published by the Indian Standard Institution and all other codes/standards which may be published by them before the acceptance of the Contract shall apply and govern in respect of design, workmanship, quality and properties of materials and testing.

Contractor to provide:

The Contractor shall provide a notice board, on proper support, 3.00M X 2.00 M in a position approved by the Architect. He shall paint, as approved by the Architect, the name of the work with cost, name of the Architect, Contractor etc. All letters except that of the name of the work shall be in letters not exceeding 50MM in height.

Independent Test Analysis:

The Contractor shall, if required by the Architect, arrange to test materials and/or portions of the works at his own cost from the test house or analyst approved by the Architect, including transport in order to prove their soundness and efficiency. If after any such test the work, or portion of the work is found in the opinion of the Architect, to be defective or un-sound, the Contractor shall pull down and re-execute the same at his own cost to the satisfaction of the Architect.

Contractor to include in his Rates:

The Contractor has to make provision in his rates for the following expenditure in his rates, other than set in the conditions of Contract:

1. Cleaning of the site before starting the work and after completions of the work including disposing off the debris out side 
     the site.

2. Welfare of his employees and laborers including accommodation, water supply and proper sanitation.

3. Expenditure regarding the foundation laying or such functions including cost of providing the memory stone as prescribed    

                    by the Architect.

4. Expenses towards permanent water and electricity supply installations. 

5. Lighting of the premises and clean maintenance of the premises during the period of construction including the labour 
    colony.
6. The Contractor shall at its own cost provide Office Space fully furnished for the Client and PMC/Engineer-in-Charge for the duration of the Contract. 

SPECIFICATION FOR RCC WORKS:
The work shall carried out as the following Indian standard codes (latest versions)

1.
IS 2502 - 1963 Bending and fixing of bars for concrete reinforcement.

2.
IS   456 - 1978 Plain and reinforce concrete.

3.
IS   432 - 1960 Mild steel and medium tensile steel bars for concrete reinforcement.
4.
IS 1786 - 1966 HYSD steel.

In addition the above specifications, following conditions are required to be followed:

a)
To avoid settlement of concrete, it is necessary to complete the compaction of lithe murum filling under the floors, prior to erection of the formwork for slabs and beams.  It is preferably to complete the PCC under the floors before the formwork is erected.

b)
The surface of the form work likely to come in contact with the concrete, shall be treated with soap solution, mould oil or any other approved material so that concrete when laid, will not stick to the form work; thereby facilitating easy removal of the forms.  The treatment should be carried out sufficiently before laying of the reinforcement.  The forms should be watered prior to pouring of concrete.  Care should be taken to prevent reinforcement coming in contact with any oily substance.  If however, this does happen gunny bags etc., may be used.

c)
The steel shall be placed exactly in accordance with the drawings and instructions and shall be properly tied, to form a rigid grilling which will not be disturbed during the concreting operations.  The splicing shall be kept to a minimum, the joints should be well staggered and so arranged that any given section a minimum of 2/3rd of the bars should be without laps.  For splicing of bars of 20 mm dia. & above approved type of welded joints shall be used No ‘extra over’ shall be allowed for the welding.  For bars less than 16mm splicing is to be done by overlapping.  Where concrete dimensions are very small, hooks, in the directions of greater dimensions can be provided.

d)
Concrete shall not be cast unless the reinforcement as laid has been checked and certified by Architects or their authorized representatives.  Architects should be intimated sufficiently in advance regarding the schedule of concreting certain part of the building so as to allow them adequate time for making the necessary arrangements for checking of the reinforcement, from work centering, etc., and also for supervising the actual concreting operation.

e)
Concrete shall be vibrated carefully until all the entrapped air is expelled.  All members of concrete shall first be vibrated by Emerson vibrators and then, by surface vibrators followed by manual ramming. 

f)
Concrete mixed designs:  For concrete of grade below M15, nominal mixes may be used.  However, for concrete of M15 and above the mix should be designed and concreting iterations should be of the ‘controlled type’ (M 150 is included in the mix designs.  However, in absence of design mix for the same, a nominal proportion 1:2:4 may be used with water cement ratio of 0.45.

Following minimum quantity of cement shall be used.



Concrete:     M 15 - 300 kg. Per cum.




            M 20 - 320kg. Per cum.

                                 M 25 – 340 kg Per Cum

                                 M 30 – 380 Kg Per Cum.

The design mix, which is on weight basis, may be converted in volumetric equivalent for convenience.  Use of weight batcher is also permissible.

The mix design will be obtained from an approved laboratory, at the cost of the Contractor.

g)
Roughening of concrete surfaces should be done thoroughly, after stripping of the formwork so as to obtain proper key for plastering.

h)
The Contractor should include in his rates, the charges for fixing of metallic or other types of inserts for fixing of electrical fitting and fixture, and piping or other service. These inserts shall be fixed by the Contractor as per the drawings and the instructions of the Architect. The cost of providing and fabricating inserts will be paid separately.

CONCRETE WORKS:
01.
Scope of Work:

The contractor shall furnish all labour, materials, tools, equipment and services necessary to complete all concrete works in accordance with the Drawings and as specified herein.


Materials and works shall include, but are not necessarily limited to the following:


a) All foundations, footings and head-walls.


b) All concrete footings, columns, beams, walls etc., where specifically excluded hereinafter.


c) Floor Slabs, concrete platforms, chejjas, drop walls, staircases, parapets, etc.


d) Miscellaneous concrete items such as jumps, pits, ramps, equipment bases and manholes covers.


e) Embodiment in concrete of items furnished by Owner for example angle-frames, manhole anchor-bolts electric conduct, ducts, and pipes, foundations bolts, etc.


f) All grouting as required.

2.
Materials:
a) Cement: Cement shall be of approved brand of 43 grade ordinary Portland cement conforming to the latest IS. Specifications. All cements shall be fresh when delivered and free from lumps and otherwise undamaged.  Cement shall be stored in perfectly watertight, well-ventilated shades. The floor of the shed shall be at least 300 mm above the surrounding ground level. 
b) Coarse aggregates:  These shall be hard, crushed granite/trap stone having clean, hard, strong, durable, un-coated particles 
    free from injurious amount of soft, friable, thin elongated or laminated pieces and alkaline organic or other detrimental matters.  
   It shall be washed, if so desired by the Architect.  Aggregates shall be stored on platforms or otherwise so as to avoid inclusion 
   of foreign materials.  It shall be thoroughly wetted before being charged into the hopper of the concrete mixer.

The grading shall conform to the following as for as possible.

________________________________________________________________________________________

Nominal                                                                             Sieve Size

Size of         _____________________________________________________________________________ 

aggregate              80 mm       63 mm       40 mm       20 mm       12 mm       10 mm       No.480.   No.240. 

________________________________________________________________________________________

(in percentage)

63 mm

           100            85-100        0-30           0-50             ---              ---              ---               ---

40 mm
                   ---            100              85-100       0-20             ---             0-50           ---               ---

20 mm
                   ---             ----              100            85-100         ---             0-20         0-50              ---

12 mm
                   ---             ---                ---             100              85-100      0-45          0-10             ---

10 mm
                   ---             ---                ---              ---                100           85-100      0-20         0-50

________________________________________________________________________________________

________________________________________________________________________________________




                Use                                                                                            Size

________________________________________________________________________________________

Slabs and walls with more than 200mm thickness


          40 mm to 10 mm

Columns and girders with least dimensions of 300 mm or more.                                    40 mm to 10 mm

Slabs and walls under 200 mm in thickness                                                                    20 mm to 10 mm

Columns with least dimensions under 300 mm
                               20 mm to 10 mm

________________________________________________________________________________________

Note : The sieve sizes of 80mm, 63mm, 20, 12mm and 10mm will correspond roughly to B.S. sieve sizes of 3”, 2 1/2”, 3/4”, 1/2” and 3/8” in respectively.


c)
Fine Aggregate:  Shall consist of natural sand or crushed stone sand or a mixture of both passing IS. 480 sieve.  The fineness modules of sand used shall be between 2.6 to 2.8.  Sand shall be sharp, coarse, clean and of approved quality and free from earth, dust or other impurity.  Sand shall be washed and/or screened if required in the opinion of the Architect. The grading shall conform to the following as far as possible.

Grading Limits for Fine Aggregates (IS. 383)

________________________________________________________________________________________ 

Sieve No.                     Equivalent                               Natural sand or                      Crushed stone

                                    B.S. sieve No.                         Crushed gravel sand                         sand

________________________________________________________________________________________

480
                                 3/6 in                                     95 - 100                                    90 - 100

240
                                    7 in                                     75 -   95                                    60 -   90

120
                                  14 in                                     45 -   85                                    40 -   80

  60
                                  25 in                                     25 -   60                                    20 -   50

  30                                   52 in                                       5 -   30                                      5 -   30

  15                                 100 in                                       0 -   10                                      0 -   15

________________________________________________________________________________________

Limits for impurities in aggregates (I.S.383)

________________________________________________________________________________________

Clay, silt and fine dust in :

Natural sand or crushed 

gravel sand (by weight)                                                                  4 percent                              1 percent

Crushed stone sand (weight):                                                        10 percent                             1 percent

Organic impurities:                                                                         The solution obtained by emerging the 





Sample in 3% solution of sodium hydroxide 





 For 24 hours should be of light color.


d)
Water : Shall be clean, fresh free from injurious amounts of acids, alkalis, oils or any other deleterious matter.  If it is from sources other than a town protected water supply scheme, such sources shall be got approved by the Architects.  It will conform to ISI - 456.


e)
Reinforce steel:  Shall be of tested quality, mild steel bars or high strength deformed bars such as torsteel or T.M.T., Fe-500 grade, complying with the latest Indian Standard specifications. They shall be clean and free from rust, scale, paint or other harmful coatings. Splitter bars or bars coated with paint, etc. will be rejected. 
All reinforcement steel shall be used in accordance with the latest I.S. codes such as I.S.  456 - 1978, and related codes.  Welding shall be used to provide splicing for bars 20mm and above (both inclusive) No extra over shall be allowed for this.  Wire used for tying and securing reinforcing steel shall be galvanized, annealed, soft iron wire of gauge No. 16,2 wires shall be used for tying, at one place.

3.
Concrete strength: Strength of concrete required for the following nominal mixes shall be as under:


1)
Nominal mix M-20 grade at 28 days shall not be less than 200 kg/ sq.cm.


2)
Nominal mix M-25 grade at 28 days shall not be less than 250kg/ sq.cm.


3)
Nominal mix M-30 grade at 28 days shall not be less than 300kg/ sq.cm.

Test cubes shall be taken, generally from each 20 cum of concrete poured during the progress of the work, or when a day’s concrete work does not amount to 20cum, as required by the Engineer in charge.  From each days quota, 6 samples shall be taken each time for testing.  3 samples shall be tested at 7 days and 3 will be tested at 28 days the strength achieved at 7 days shall not be less than 2/3 of the 28 days strength.  The cubes for the tests shall be 150 mm X 150 mm X 150 mm ( 6” X 6” X 6” ) and will be tested as specified in I.S. 456-1964 Table 5 “Acceptance criteria for concrete”  The result of tests in any of the recognized laboratories shall be taken as final and binding on the contractor.  All arrangements for testing concrete cubes shall be made by the Contractor.  All the materials and labour for making curing and transporting the cubes for necessary tests including the cost of testing shall be at the cost of the Contractor.  Normally cube strengths, substantially in excess of those specified, are expected.

In case the compressive strength obtained from the test cubes of concrete, is less than the minimum specified strength the work is liable to be rejected.  If however, the strengths are higher than specified due to good control or otherwise, the Contractor shall have no claim for extra payment.

4.
Batching of Concrete Mixes:

a)
Proportioning Limitations:  The mix shall be adjusted to obtain the requisite workability as measured by the slump test.  The slump in general shall be as follows for various Uses of concrete:



Mass Concrete                           

50 mm



Floor Slabs                                                           

50 mm



Roads and Payments (machine finished)
    
25 mm



Heavy reinforced sections
   
50 mm



Thin vertical reinforced sections and columns    

100 mm


b)
Cement and aggregate measurement:  Aggregate shall be accurately measured by measuring boxes.  Cement shall also 


be measured by measuring boxes and shall not be used directly from bags.

c) Water Measurement:  Water measurement shall be by volume or by weight provided that the measuring device can be 
maintained so that its inaccuracy will not exceed one percent.  Total water shall include all surface water carried by the aggregate.

5.
Mixing:
Concrete shall be machine mixed, in a batch mixer of approved type, which will ensure a uniform distribution of the material through the mass, so that the mixture is uniform in colour and homogeneous.  The mixer shall be cleaned at frequent intervals while in use.  The mixing of each batch shall continue not less than 1 1/2 minute after all the material and water are in the mixer during which time the mixer shall turn at a speed of about 60 revolutions per minute.  The volume of the mixed materials per batch shall not exceed the manufactures rated capacity of the mixer.  Concrete shall be poured and consolidated in its final position within 20 minutes of mixing.  The re-temping of concrete which has partially hardened i.e., remixing with or without additional cement, aggregate or water shall not be permitted.
6.
Formwork:
All forms for concrete work shall be neatly constructed of finished lumber surface on the side in contact with the concrete except that the forms for the concrete which will be exposed shall be of planed timbers.

Forms and centers shall be clean, watertight, substantial and sufficiently braced to maintain their proper position during the placing, or vibrating of the concrete.  Joints in forms shall be horizontal or vertical and shall be close enough to prevent leakage and loss of mortar.  Forms once used shall have nails withdrawn and surface to be in contact with concrete thoroughly cleaned before using again.  Forms shall be set to line and grade and so constructed and fastened as to produce true lines.

Temporary openings shall be provided at the base of columns and wall forms and other places where necessary to facilitate cleaning and washing out of debris and inspection immediately before depositing concrete.

Forms shall be designed and constructed in such a manner so as to permit removal of sides, leaving the bottoms of members undisturbed.  The centering and props for the various members shall be fixed in a workmanlike manner to be approved by the Architects.  They shall be of such sizes as the Architects think fit and proper.  The centering shall be removed only after permission to that effect has been obtained from the Architects props shall not be less than 75 mm dia. on top and shall be supported on wedges.  Planks shall not be less than 35 mm thick.  For supporting the roof slab of the vault, the centering planks, runners and props, shall be of such dimensions as approved by the Architects.

The minimum period for keeping the centering in position and for watering after laying the materials shall be as follows:

                                                  Centering                               Curing
Slab in general:                          10 days                                  To be done for 21 days and the concrete to be 




                                                                                  protected from direct rays by spreading non-




                                                                                 conducting  materials over it.

Under-side of beams:                  21 days                                            ------ do ------

Side of beams:                              2 days                                            ------ do ------

Columns:                                       1 day                                    
  ------ do ------


      

Lintel Sides:                                  2 days                                            ------ do ------

Lintel bottom:                              15 days                                             --- -- do ------

Coping:
                                         1 day                                            --- --do -------

Vault roof slab:                            10 days                                             ----- do --------

No centers of forms shall be struck or removed until the concrete placed therein has developed sufficient strength to safely support the loads imposed thereon, and at all times, the consent of the Architects shall be obtained before forms are removed. Under no conditions shall forms, centers, shoring etc. be removed from the above items until the minimum time as specified for the items has elapsed.


Extreme care shall be exercised in removing from to avoid injury to the concrete.

The framework shall be so constructed that the maximum permissible deviation of the finished concrete shall not exceed 6 mm vertically and 12 mm in horizontal plane from the theoretical line.

The forms/shutters are to be applied with approved make de-shuttering compound before placing in position. Use of black waste oil for shutters is not allowed.
7.
Placing Reinforcement:
Reinforcing bars shall be accurately bent cold and sized and located as shown on the drawings.  No reinforcement shall be bent or straightened in a manner that will injure the material.  Bars with kinks or sharp ends shall not be used.

Bars shall be accurately set and held in place by system of bar chairs, bolsters, wire ties of not less than 16 gauge.  Spacing and location shall be as shown on drawings.

Blocks of concrete to hold the reinforcement in proper level shall be of relevant strength.  The clear spacing between bars shall be not less than 1 1/2 times the maximum size of the coarse aggregate or not less than 25 mm or as may be specified otherwise by the Architect.

8.
Placing Concrete:
Before placing concrete, the forms shall be thoroughly cleaned of all chips, shavings etc., concrete shall not be 
deposited in standing water.

Concrete shall be thoroughly worked around reinforcement, embedded items, and into the corners of the forms.  
Concreting shall be carried on at such a rate that the concrete is at all time plastic and flows readily into spaces between bars.  Concrete shall be vibrated with an approved type of internal vibrator.  Vibrator shall not be left in any position for more than five (5) seconds and shall not be used against forms in slabs placed on grade, in case of needle vibrator.

Construction joints shall be located and formed as directed by the Architect and shall be such as to least impair the strength and appearance of the structure.  Sufficient sections shall be provided in the keys to resist shear. Construction joints in column capitals shall be considered as part of the built monolithic with the floor construction.

9.
Protection:  All the concrete shall be adequately protected from mechanical or other damage for at least seven days.

10.
Defective Concrete:  If any concrete is found defective in strength, not true to line or level, or is poured out of 
position, the Architects may direct that such concrete be removed and replaced or that other protective measures be taken as he determines.  All such repairs and replacement shall be carried out at the Contractor’s cost if any load tests are required to be conducted on a concreted member the same shall be got done at Contractor’s cost.

11.
Curing of Concrete: Concrete surfaces, exposed to air, shall be kept free from excessive drying by the use of 
continuous water spray, bunding, weight burlap cover or an approved curing compound for a period as specified continuously after the concrete is placed, if the curing compound shall be of the resin base type that is not detrimental to the applied part.

12.
Finishing Concrete:

Slab and Floor Finishes:
a) Wood Float Finish:  In finishing the tops of concrete slabs which are exposed to weather the forms shall be completely filled with concrete and the surface brought to grade with the little working as possible.  Tolerance greater than 1 mm to 1 meter of surface will not be permitted.  The surface shall be wood floated until it is free from blemishes and gives a smooth appearance.


b) Floors:  Floors shall have a hardened finish, which shall be accomplished as follows:

After the forms have been filled with concrete and the surface has been brought to a true plane by means of ‘Jitters Buffing’ bull floating and wood floating, the floor shall be given a medium sweat finish with hand and or machine steel trowels and allowed to cure until perfectly dry.

A hardener solution or compound shall be applied where indicated strictly in accordance with manufacturer’s recommendations.


c) Walls and Ceilings:  Shall be form finished where indicated otherwise as per (d) and (e) here in after.

d) Other surfaces: On all other surfaces, all voids and honeycombs shall be patched after forms are removed.  Patching shall be done by chipping and scarifying the defective area, and filling with grout composed of one (1) part of cement and two (2) parts of sand (by volume).  The surface to be patched shall be thoroughly wetted before applying the grout.  Patched areas shall match adjacent concrete in appearance.

e) Finishing with plaster:  All concrete surface which are to receive cement plaster shall be hacked 7 mm to 10 mm deep with minimum 100 hacks per sqm.

13. 
Bonding and Construction Joints: Before depositing new concrete on or against concrete which has set, forms shall be tightened and old concrete surface shall be roughened cleaned and drenched thoroughly with water.  Reinforcing steel shall be cleaned of all dried cement mortar and loose mill scale. The concrete joint to be applied with a coat of Nitobond-Ep or equivalent bonding agents, before pouring new concrete. 

Concrete in each unit of construction shall be placed continuously, construction joint locations will be as shown 
on the plans or as approved and shall be kept to a minimum consistent with sound construction practice.

All construction joints shall be made ‘Water tight by the use of key ways grouted with cement mortar.  A layer of cement mortar (1:2) mixed or as specified should be laid over the surface of the old concrete before placing new concrete there on.  Where shown on plans, water stops shall be provided.

14.
Grouting of steel column Bases:
All column base plates shall be grouted with cement mortar mixed 1:2 to a thickness as specified and shall be mixed as thickly as possible consistent with fluidity.  It shall be consolidated by thoroughly ramming with suitable blunt hammer, until the space has been completely filled.  Non-shrink adhesive, where indicated, shall be provided as per manufacturer’s recommendations.

15
Anchors, Sleeves, Inserts etc.:
Embed into the concrete, all the necessary anchors, sleeves, inserts, wall ties etc. as may be required for the 
installation of other work.  All such items will be furnished to the contractor by other with the necessary instructions and templates for their placement.  Bolts shall project from the face of the concrete, the distance called for on the details or a sufficient distance to allow for the proper attachment intended.  All threads shall be oiled and protected by water proof caps.

16.
Clean-up:


Any and all work of this and/or other traders soiled or damaged in the execution of the work under this section of the specification shall be thoroughly cleaned, repaired and replaced, periodically during the construction and immediately after the completion of the work covered by this section of the specification the Contractor shall remove all the scrap material, debris etc. remaining from his work from the premises leaving the premises in a clean and orderly condition.

17.
Measurement:
All concrete work shall be measured and paid for as per I.S. 1200 specifications pertaining to the method of measurement of building work.

BRICK WORK:

Mortar Preparations:      

   
Cement mortar for brick work an pointing shall be generally be as specified herein namely in proportion of one of 
cement with 6 of sand by volume, or as indicated otherwise.  Mortar shall be prepared by mixing cement and sand in specified proportion in dry.  The mortar shall be used within 20 minutes of mixing.  No mortar that has begun to set shall be used.


Materials:

Bricks shall be best leading make workable B.B. uniform size, shape and colour and must be well burnt so as to 
give a clear ringing sound when struck.  They shall be clean whole and free from flaws, cracks stones or lumps 
of any kind, especially lime.  They have sharp edges and angles and even surfaces and shall be sound and hard 
to resist compression.  They shall be from a source to be approved by the Architects.


No brick after immersion in water for 24 hours shall absorb more than 15 percent of its weight.  The minimum crushing strength of the brick would be 30 kg /sq.cm., when thoroughly soaked in water and 39 kg / sq.cm. when dry.
4.
Workmanship:

All brick shall be kept soaked in water for at least 12 hours prior to use.  The work shall be set out by the Contractor. No brick bats shall be used for the work except where required to complete a standard bond.

All joints in brickwork shall be uniformly laid.  Each layer of brickwork shall be laid plumb and level and with correct break of joints. No mortar joint shall exceed 15 mm in thickness.

The works shall be kept wet for at least 10 days after laying the last course and after wards shall be watered twice a day for one month.


Brickwork shall not be raised more than 10 courses a day unless otherwise approved by the Architect.


Brickwork shall be uniformly raised all round and no part shall be raised more than 1 meter above another, at 
any time.  The Contractor shall provide all necessary openings for doors, windows or such other survives and shall embedded all fitting and fixtures (if separately paid for) at no extra cost.

       The brickwork is to be carried out with all necessary set backs, projections, cuttings, too things etc., which are 
shown on and in strict conformity with the drawings.


All uneven, irregular and bad brickwork shall be demolished if deemed necessary by the Architects and re-built 
at Contractor’s expenses.

All joints of brickwork to be plastered or pointed, shall be properly racked to a depth of 12 mm as the work proceeds.  In no case mortar which has set shall be removed from joints by hammering chiseling or any such manner so as to cause damage to the brick, but shall be raked out with a suitable metal tool before the mortar sets.


115 mm and 225 mm brick walls shall be built fair faced on one side only.  All other walls of greater thickness shall be built without exception with fair face to both sides.


Where specifically indicated, 115 mm or thinner brick works shall be executed in one of the following ways.

 With R.C.C. stiffeners:  Brick work shall be carried out in panel measuring approximately 1.5 x 1.5 m with R.C.C. (1:2:4) verticals of 12 cm x 12 cm and horizontal stiffeners 12 cm x 8 cm both reinforced with 4 nos., 6 mm dia. bars laid in (1:2:4) concrete properly filled in and cured.  Such R.C.C. work shall not be measured separately but will be included in the rate for brickwork.


In lieu of hoop iron, the Architects may direct the use of mesh or M.S. bars as reinforced.

STONE MASONRY:

Stones shall be set level, plumb, with uniform joints set in full bed of mortar, with joints filled. The joints should not be more than 25 mm.


All stones to be well wetted except in frosty weather, Rake out mortar joints when setting.


Utmost care shall be taken during construction that surface of the stones is not spoiled by concrete or mortar dropping on the stones.  The surface of the stones shall be immediately cleaned with water if any 
concrete or mortar does fall on the stone faces.


Stones for masonry shall be best hard stone, locally obtainable from approved quarries.  The masonry, wherever 
required, shall be composed generally of large stones clean flat bedded, properly selected for their places and 
carefully laid, with a suitable proportion of smaller stones and chips to fill up the interstices.  The whole work 
shall be hand set and solidly bedded in and surrounded with mortar on every side except the face.  There shall 
be no hollows or dry portions in work nor pinning in the face.  The face stone shall be flat-bedded, shall tail back 
and be bound well into the body of the wall and shall not be of height greater than either the breadth of face or length of the tail.  Through stones, covering the whole width or thickness of the walls of 60cm, long where the walls are thicker than 60cm shall be inserted at every meter measured horizontally and vertically.  The rates for rubble masonry shall include the extra cost of the through stones.  The face of the wall shall be shaded from the sun and kept well moistened for at least 10 days after completion.


The height of course shall not exceed 60 cm in a day.  When the work is stopped on the day or on holiday or 
when up to its full height, tables shall be formed on the surface with cement mortar and kept full


Selection of proper stones, breaking of boulders, etc. in case the wall is to be constructed from stones available 
at site, scaffolding if necessary, racking out joints, preparing mortar tables for stagnation of water for curing etc. should be complete.




                                          FLOORING SKIRTING AND DADOOING:
Ceramic tiles flooring and Dadooing:
Ceramic tiles shall unless otherwise indicated be 300 mm X 300 mm X 6 mm thick in size for flooring and of 200X300X6mm for dadooing, and of best quality, Indian make obtained from approved sources.

 Shahabad/Cuddappa/Kota/Polished Granite flooring / dadooing : 

Shall be of selected quality, hard, sound, dense and homogeneous texture, free from cracks, decay, weathering and flaws.  Stone slabs shall be of uniform colour and as approved by the Consultant.  They shall be machine cut and machine polished where specified and shall conform to the required sizes.  Thickness shall be as specified in the respective items. The slabs are to be of approved size and of approved shade as approved by the Architects.  


Measurement will be made in square meter of area covered. 

 WOODWORK, CARPENTRY, JOINERY AND PAINTING:
1.
Timber:

Timber to be sound, bright and well conditioned, clean, free from waves, injurious open shapes, large loose or 
dead knots, and cut square and straight all to be thoroughly seasoned and with only a very small proportion of bright san and no discoloured sap whatsoever, will be allowed.  The whole of the timber to be cut into required scanting’s at least three months before being framed.  Timber shall generally conform to the Indian Standard specifications.


Scantlings of all types of timber shall be straight. Warped scantlings shall not be used.  Before use on the work, 
the scantlings shall be kept kept in a covered and well ventilated place and shall be placed in alternative longitudinal and transverse layers with air spaces of not less than 25 mm between them.  The sizes of scantlings will be as per drawings, after the frames are made.

2.
Workmanship:
The workmanship shall be of the best quality.  All ‘Wrought’ timber is to be saw planed, chipped or otherwise machine worked to the correct sizes and shapes indicated on the drawings or as specified.  The finished scantlings shall be of uniform width an thickness throughout.  Where the nominal dimensions are stated for ‘Wrought’ timber, an allowance of not more than 1.6 mm shall be permitted for each ‘ Wrought’ surface.

All carpenter’s work shall be accurately set out and framed together and securely fixed in the best possible manner and with properly made joints.  All joints must fit accurately, without welding or fitting.  All nails, screws, plugs, pins etc., shall be provided as necessary and as directed and approved.  After the woodwork has been erected, if any under shrinkage or bad workmanship is discovered the contractor shall forthwith, amend the same without any extra charge.

The joiner shall perform all necessary mortising, tenoning, grooving, matching, tonguing, housing, riveting and all other works necessary for correct jointing.  He shall also provide all metal plates, screws, nails and other fixings 
that may be ordered by the Architect or that may be necessary for the proper execution of the joinery work 
specified.  Joiner work specified.  Joiner shall also carry out all works necessary for the proper construction of all framings, linings etc., and for their support and fixing in the buildings.


Joinery shall be constructed exactly as shown on the drawings or as instructed by the Architect.  Where joints and are not specifically indicated, they shall be the recognized from of joints for each position.


Loose joints are to be used where provision must be made for shrinkage or other movements acting, other than 
in the direction of the stresses of fixing or leading.

Glued joints are to be used where provision need not be made for shrinkage or other movements in the connection and where sealed joints are required.  all glued joints shall be cross tongued or otherwise reinforced.  all nails, springs etc. are to be punched and puttied.  All surface to be glued or to be kept clean, free from dirt, dust, sawdust, oil and other contamination adequate pressure should be applied to glued joints to ensure intimate contact, the same is to be maintained while the glue is in settings.


All skirting, architraves, plates and other joinery works shall be accurately scribed to fit the contour of any irregular surface against which they may be required to form a close, butt connections.


The joiner shall take all necessary measures to check or prevent capillery penetration of water in the joints and open connections of external joinery works, and in all other positions where joinery works may be exposed to water.

The joiner shall ensure that all weathering surfaces, throatings, grooves and joints etc., and all open connection in external joinery works shall be properly executed and shall obtain a reasonable degree of weather resistance. The doors and windows shall be provided with M.S. holdfasts out of 50 mm x 6 mm thick flats fixed in to the james of walls and embedded there in cement concrete 1:2:4.  The number of holdfasts shall be as indicated in the drawings.  Wherever necessary, rawl plugs, bolts etc. shall be used for fixing, framing etc.  Iron screws shall be used unless otherwise indicated. 


All exposed woodwork in country teak shall be painted with three coats of oil paint of approved make, quality and shades. 


All woodwork in contact or embedded in masonry work shall be treated with two coats of solignum or coal tar as 
directed by the Architect, prior, to installation.  Other area of woodwork is to be applied with a coat of wood primer before installation.

3.
Fixtures and Fastenings:

The scale, quality, materials and workmanship of all fixtures, and fastenings shall be as indicated in the Bill of Quantities and drawings and drawings or as directed by the Architect.


All fixtures and fastenings shall be new, sound and strong.  They shall be of best quality.  The size, shape, designs and finish shall be as shown on drawings and approved by the Architect.  Samples of all fixtures and fastening shall be got approved by the Architect and shall be deposited in the Architect’s site office for reference.


All fixtures shall be fixed to be joinery in a secure and efficient manner.  And of the fixtures damaged during fixing, shall be replaced by new ones in their place and the surface of joinery made good where affected, at the Contractor’s.  Metal sockets shall be provided to all bolts where the shoots enter brick, stone, concrete etc. These shall be securely fixed flush with the surface into mortises and cemented.  Mortise plates over holes shall be used in situations where the shoots enter wood, parliamentary hinges shall be used when so shown as in the drawings as required or as directed by the Architect. But and similar hinges shall be counter sunk on the leaf edge and wood frame to a depth equal to the thickness of the flaps of the hinges. 


Details of fittings & fixtures to be provided: (per door)

Holdfasts made out of 40mm X 6mm M.S. flats: 250mm long: 6 nos.


250mm X 16mm heavy duty C.P. Alldrops       : 1 no.


125mm long heavy duty C.P. handles              : 2 nos/shutter.


125mm/150mm (depending upon the shutter size) iron oxidised I.S.I. Butt hinges: 

                                    Single shutters                    : 4 nos.

                                    Double shutters                   : 3 or 4 nos.


2000mm X 10mm Al. heavy duty tower bolts    : 2 nos/shutter.


Heavy duty brass door stoppers                       : 1 no. per shutter.


Rubber/plastic bushes                                      : 2 nos. per shutter.


250mm X 16mm C.P. latches                           : 1 no.

All the fittings & fixtures for part glazed & part paneled entrance doors are to be of ornamental type brass including the hinges.

10.
The rate of wood to include the cost of the following in teralia:

· Providing and fixing of various fittings and fixtures.

· Painting, applying wood preservatives etc.

· Screws, nails, holdfasts etc.

· Fixing and erecting in position all woodwork.


Woodwork in general shall be measured as per IS. 1200 unless items of the Bill of Quantities.

WATER PROOFING AND ALLIED ITEMS:
1.
Water proofing of roofs (flat, sloping or curved ) with Bituminous felts:


a)
Scope of work:  Providing laying and finishing members or coating as per manufacturer’s specification 


including all materials, labour, scaffolding, tools and equipment’s etc., all complete.


b)
Materials:  Cement and sand shall conform to IS 269 and IS 1542 respectively.



Water proofing compound shall be of approved make and quality of tar felt as per IS 1322.

The bonding material shall consist of blowen type bitumen confirming to IS 702 or residual bitumen conforming to IS 73 or a mixture there of, selected to withstand local conditions of prevailing temperature and gradient of roof surface. The penetration of bitumen shall be limited to 40 when tested in accordance with IS 1203.

c)
Workmanship: Work shall be carried out as per clauses 5.01, 5.02, 5.03, 5.04 and 5.05 of IS 1346.

The normal treatment of waterproofing as outlined in clause 6.02 of IS 1346 shall be rigidly adhered to.  The sequence of laying shall also conform to clause 7 of IS 1346.

2.
Expansion joint filler material:

a)
Scope of work:  Work includes providing and fixing expansion joint filler material between columns, in roofs, in floors and walls as shown on drawing including scaffolding, tools so as to complete the job in all respects.


b)  Materials:
Bituminous Expansion joint filler:  This shall be fiber board of required and of approved make such as ‘Shalitex’ Shalimar expansion joint filler, or equivalent.


Sealing compound and primer:  This shall be of approved quality such that produced by Shalimar Tar Products 
(1935) Ltd., or equivalent.


c)  Workmanship:  The entire work shall be carried out strictly as per manufacturer’s specifications.  The fibrous board shall be trimmed to correct size as shown on the drawing and shall be secured in position without any distortion horizontally or vertically.  The sealing compound shall be heated and placed as per manufacturer’s 
specification on the primer, splied to the jointing surface to the desired depth and length.  The exposed surface of the sealing compound shall be finished off in the form as shown on the drawing.


All the stains of the sealing compound on the brick or concrete surface shall be removed.

 SPECIFICATIONS FOR PLUMBING AND SANITARY WORK:
1.
Stone Ware Pipes:

Drains shall be laid in straight lines and to even gradient as shown in the drawings.  Adequate care shall be exercised in setting out and determining the levels of the pipes and the contractor shall provide suitable instruments templates and equipment necessary for the purpose.

The pipes before being laid, shall be thoroughly cleaned, specially for each joint, sufficiently long to entirely surround the spigot end of the pipes, the gasket to be driven as far as possible in to the joining by means of a suitable instrument.  The spigot shall be centered in the socket and after the joint has been thoroughly cleaned 
and moistened the socket shall be filled with neat cement paste, which shall be splayed off to form a neat filled around the pipe.  Each pipe shall be properly bound in, so that the invert is to a true and even gradient.  Wherever practicable, all main drains shall be commenced at the point of the out fall the necessary joints for the branch drains being inserted as the work proceeds until the mains are complete.  The branch drains shall then be commence at the point of their junctions with main drains.  The whole of the drainpipes shall be accurately laid and butted closely together at the joints.  Any earth, cement or other material entering the pipeline shall be thoroughly cleaned out of the pipes as the work proceeds.


After sufficient interval has been allowed for the joints to set, and before filling the trench, the joints of the pipes 
and drains shall be proved water-tight by filling the pipes with water to a level 2 meter above the top of the highest pipes in the length to be tested closing the ends of the sections and maintaining this water level for a period of one hour.  If the testing is to conform to the regulations of the local authorities it shall be done accordingly, to the satisfaction of the local authorities.


All such testing shall be done wholly at the Contractor’s expenses inclusive of apparatus, provision of water etc.  
and the rate covers all the above works.

2. Gully trap: Gully trap shall be 150 mm x 150 mm or any other size, glazed stone are, laid on 15 cm.  P.C.C. (1:3:6) bed with cement plaster rubbed smooth.  A full size 300 mm x 300 mm or as specified cast iron frame and over, painted two coats hot tar, shall be fixed securely on top.  The rate includes all these works as specified.

3. Closets:

Closets shall be earthenware of fire clay, glazed inside and outside.  The bore of water shall be large and the depth of the seal shall not be less than 50 mm or as specified.  


The seat of European closet shall be of plastic/PVC of approved make and colour.


A sample shall be approved by the Architect before supply is affected.


4. Flushing Cisterns:
Where not specified, the flushing Cisterns for W.C.S. and urinals shall be of best quality as approved by the Architect.  The cisterns shall be hard plastic/PVC painted white ‘Duco’ spray paint where specified and with 
cover and bracket etc., complete.  The capacity of cistern for Indian/European closets shall be (10 liters) cisterns of European type closet shall be of ‘Low’ type and approved make.  They shall be fitted with unions for connection, to lead service pipes. The flush pipes shall be fixed with a slope not less than 40. Over flow from flushing cistern shall discharge in to open, clear of the building.


5. Mode of Measurement and Payment:  The contract shall be for one meter of pipe length as laid including 
specials.  The length shall be measured net on straight and curved sections along the center line of the pipeline per pipes and specials, correct up to one centimeter. 

         6. Materials:


a). Water closets, Urinal pans, Washbasins etc: Hindustan/Parryware/Cera/equivalent approved make.


b). C PVC  pipes: ‘ASTRAL’ / equivalent approved make.


c). Fittings and accessories: ‘ASTRAL’ / equivalent approved make.

d). Rigid PVC PEHD water supply pipes: Prince/Oriplast/equivalent approved blue pipes.


e). Rigid PVC soil pipes and fittings: Prince/ Supreme make.


f). C.P. fittings & fixtures: Mark/Jaquar / Mark / Ess-Ess /equivalent approved make.

All sanitary-plumbing materials are to be got approved by the Architect before using it at the site.

SPECIFICATIONS FOR ROADS :    

These specifications shall apply to all such highway works as required to be executed under the contract or 
otherwise directed by the Architect.  In every case the work shall be carried out to the satisfaction of the Architect and conform to the location, lines, grades and cross-sections shown on the drawings or as indicated by the Architect.  The quality of work and materials shall comply with the requirements set froth in the succeeding sections.  Where the drawings and specifications describe a portion of the work in only general terms and not in complete detail, it shall be understood that only the best general practice is to prevail, materials and workmanship of the best quality are to be employed and the instructions of the Architect are to be fully complied with.
Note: 5% percentage wastages on all issued materials will be allowed; wastages above these limits will be recovered from the contractor at market rates.
ELECTRICAL WORK: 
A.        WIRING SYSTEM

           SCOPE

1.1      The scope of work under this section generally covers internal wiring for lights, fans, exhaust fans, call bells, fan coil units, geysers, power sockets etc., The contractor shall provide all materials, labour, equipment,  scaffoldings, etc., as required for the completion of wiring installation called for.   The wiring shall generally be done using PVC insulated copper conductor wires in PVC/M.S./G.I conduit as called for including providing switches, sockets, plug tops, fan regulators, outlet boxes etc., 

1.2       STANDARDS APPLICABLE
1.2.1    The applicable standards for above work shall be as listed below:

          IS: 732     Code  of  practice  for  electrical   wiring  installation (System voltage  not  exceeding  650 V).

          IS : 1646    Code   of  practice  for  fire   safety   of  buildings (General Electrical installation).

          IS : 2667     Fittings   for  rigid  steel  conduits   for  electrical wiring.

          IS : 3480     Flexible   steel  conduits  for   Electrical wiring.

          IS : 3837     Accessories  for  rigid  steel  conduit  for  electrical wiring.

          IS : 694       PVC insulated cables.

          IS : 2509     Rigid - non-metallic conduits for electrical wiring.

          IS : 6946     Flexible (Pliable) non-metallic conduits for electrical installation.

          IS : 1293     3 Pin plugs and sockets.

          IS : 8130     Specifications  for conduits for  electrical installation.

          IS : 3854     Switches for domestic purpose.

          IS : 3415     Fittings for rigid non-metallic conduits.

          IS : 4648    Guide  for electrical layout in  residential  building. 

          IS : 9537    Conduits for electrical installation.

          IS : 302      General   and   safety   requirements    for  household and similar electrical appliances.

          IS : 3043     Code of practice for earthing.

          IS : 5216     Guide for safety procedures and practices in electrical work.

                               Indian Electricity Act and Rules. 

           Regulations  for the electrical equipment in  buildings  issued  by  the Bombay Regional  Council  of  Insurance association of India.

            All standards and codes mean the latest.

1.3       POINT  WIRING  FOR  LIGHTS, FANS,  EXHAUST  FANS  & 5A CONVENIENCE  SOCKETS

1.3.1   A point wiring shall consist of the branch wiring from  the  distribution  board  together  with  a  switch/fan   regulator  as required, including providing conduit and  accessories,  the ceiling rose or pendant holder  or  a  swan  holder, or ceiling fan hook box or  socket  etc., with  suitable  termination.   Point wiring shall include, in addition, the earth continuity conductor/wire from the distribution board to the earth pin/stud of the outlet/switch box and to the outlet points. 

The point wiring shall be carried out in the under mentioned manner:

a)  Supply, installation, fixing of conduits and GI pull wire with   necessary   accessories,   junction/pull/inspection/switch  boxes and outlet boxes/Fan hook  box etc.  Switches, switch plates and switch boxes are not required for the lights which are controlled directly from the MCB DB's.

b) Supplying and drawing of wires of required size including earth continuity PVC insulated wire.

c)        Supply,  installation  and connection  of  flush  type switches,  sockets,  cover plates, switch  plates,  and  fixing fan regulator, lamp holder, ceiling rose etc.,

d) The point shall be complete with the  branch  wiring  from  the  distribution  board  to  the  outlet  point, through switch  board,  conduit   with   accessories,  junction,  pull,  inspection  boxes,  control   switch, socket,  outlets boxes, ceiling  roses,  lamp  holder, connector, extension cord wire, flexible conduits etc.,

1.3.2    POINT RATE
           For purposes of measurements and payments the rate  for  point wiring for lights/fans etc., is divided into  two parts.

          a) Circuit Main

          b) Point Wiring.

a)        Circuit Main for Light/Fan Point

The circuit main for lights/fan/6A sockets  (where 6A sockets connected to light circuit) shall include the wiring  from the MCB distribution boards upto the first switch/light point/fan point.  This is measured in linear meter.   The scope of work under this section shall include

           i)  Supply and  wiring in concealed/surface  conduit  from  DB's to first switch/light/fan point.

           ii) Providing and installing PVC insulated copper conductor earth wire. 

           iii) Providing and installing GI fish wire (pull wire) in the conduit.

           iv)  Termination of wires in DB's and switches using proper tinned copper lugs of crimping type. 

           v)   Providing and installing necessary pull/junction boxes   where necessary. 

 Point Wiring

b) The rate for point shall include supply, installation, and connection, testing and commissioning of point wiring in conduit.  The points shall be measured in No/sets for the set/group of lights controlled as mentioned in SOQ.   

           The exact scope of work included in the point wiring for the purposes of measurement is enumerated as stated below 

 i)      Wiring starting from the first switch/light/fan point, where the circuit main is terminated to the various lights/fans/sockets  (where 6A sockets connected to light circuit loop), and then looping between the switches/lights/fans/6A sockets etc.,

  ii)    Providing and installing all necessary switches, switch  plates,  sockets, pull/junction/fan hook boxes etc.  as called for. 

 iii)      Providing  and  installing insulated  earth  continuity wire in each conduit along with the wiring system. 

  iv)     Providing and installing G.I. fish wire (pull wire)  in  the conduits. 

   v)     Providing  and installing ceiling roses,  lamp  holders where necessary.

 vi)     Providing  and installing PVC insulated,  PVC  sheathed  flexible three core 1.5 sq.mm extension cords including flexible conduits from light/fan outlet points  mounted  at ceiling point to the light/fan outlet. 

           Wiring   for  6A  Sockets,  16A  Power  Sockets   for  Equipment    Wiring

          Except where 6A sockets connected to the lighting  loop  which are measured in Number of points, the measurement  for  wiring  of  6A/16A sockets and  wiring  for  power  outlets is done as follows :

   i)      Length  of circuit wire including conduit,  accessories  and earth wire for power wiring is measured together in linear metre.

  ii)      The  socket  outlet  with outlet  box  is  measured  in  Numbers. 

1.4.0    SYSTEM OF WIRING
1.4.1    Unless otherwise mentioned on the drawings, the  system  of internal wiring shall be as follows :

           The system of wiring shall consist of single core,  PVC insulated,   650/1100  Volt  grade,   stranded   copper conductor   wires/cables  laid  through  concealed   or  exposed PVC/GI/MS conduits as mentioned elsewhere or as directed by owner/consultant. 

1.4.2   GENERAL:  Prior  to laying and fixing of  conduits  and light outlet boxes, contractor shall carefully  examine the layout drawings and prepare detailed shop drawings, indicating  the exact location of light  outlets,  with distances  marked, conduit routing, with sizes,  number of  wires run in each conduit, control switch  location  etc.,  The contractor shall obtain the approval of  all shop drawings by the owner/consultant     prior to  the  installation  of conduits.  Any discrepancy noticed  in  the  design drawings shall be brought to the notice  of  the owner/consultant. Any suggestions or  modification suggested  by  the contractor shall  have  approval  of  Client/ Consultant before execution.

1.4.3   Type of Installation

           Unless  otherwise  specified all conduits  for  surface wiring  shall be heavy guage rigid GI/MS  conduits  and all  concealed installation including conduits  running  above false ceiling shall be heavy guage rigid PVC.

           All conduits buried in grade or in damp wet areas shall be heavy gauge G.I. conduits.

a)        Concealed Wiring shall be done using PVC conduits  in  the following areas

              i)  Staircase area lighting.

             ii)  Wiring inside offices.

            iii)  Wiring in the false ceiling area.

             iv)  All  other  areas where surface  conduit  is  not specifically mentioned.

b)       Surface  Wiring shall be done using Heavy  Gauge  G.I/Black Enamelled M.S. Conduit.

              i)   Wiring installation in  the  electrical  sub-station   room, D.G.room.

             ii)  Pump room, sewage treatment plant room.

             iii)  Ventilation fan room, AHU room, electrical room.

 c)      Conduit Installation in False Ceiling Area

          The PVC conduits shall run exposed using above false ceiling. 

1.5     MATERIALS:

1.5.1   CONDUITS

           Type of Conduit

          All  conduits  for fire alarm  system  irrespective  of  surface or concealed shall be of G.I/M.S. 

          Generally  concealed  electrical  wiring   installation shall be in PVC conduits and surface wiring in G.I/M.S. conduits. 

a)       PVC CONDUITS :
           Non-metallic conduits and accessories shall conform  to IS  9537  (part 3) - 1983, IS 2509 & IS 3419  and  each conduit shall bear the ISI Mark.  PVC conduits shall be  of  the  black, round, heavy gauge  polyvinyl  chloride (PVC).   The  conduit  shall  be  plain  end  type   as specified  in IS 2509-1973/IS 2537-1983.   The  conduit  internal  surface  shall  be  smooth.   Only   approved quality  factory made bends/accessories shall be  used.  Minimum  size of conduits shall be 20mm diameter.   PVC conduits  shall  be rigid  unplasticised,  heavy  gauge  having  minimum  wall  thickness  of  2.0mm  upto  25mm diameter conduit and 2.5mm wall thickness for all sizes above 25mm diameter. 

1.5.3  CONDUIT ACCESSORIES

          PVC CONDUIT BENDS & COLLARS
          The PVC conduit bends & collars shall be of heavy  duty  and  preferably of the same make as of  conduit.   This shall  conform to IS 9537/1983 Part III with  ISI  Mark where  necessary bends or diversion may be achieved  by means  of using bends and or circular inspection  boxes with   adequate   and   suitable   inlet   and   outlet  termination.  In case of recessed installation  system.  The  bends shall be properly secured & flush  with  the  finished  wall surface.  Elbows shall not be used.   No bends  shall  have  radius less than 2  1/2  times  the outside diameter of the conduit.

           PVC/INSPECTION/JUNCTION/PULL BOXES

            The Inspection/pull box/junction box, where used,  with  relevant  PVC  conduit installation shall be  of  heavy gauge  PVC  and conform to IS specification  and  shall match  with  the  conduit  sizes.   The  box  shall  be round/square  rectangular with conduit stub  projection  for  termination  of  conduit.  The  box  shall  be  of minimum 50mm deep and the size of box shall be suitable  to  pull/make  necessary  joints of  wires  inside  the boxes.   Extra  deep boxes are  preferred.   The  boxes  shall have flush type cover.  The colour of plate shall match  the  colour  of  paint  of  the  surface   where   installed.   The  boxes shall  have  concealed  screwed  socket for fixing the ceiling rose.

1.5.4   SWITCH OUTLET & SOCKET OUTLET BOXES

           CONCEALED TYPE OUTLET BOXES

           The concealed outlet boxes for switches, sockets, power outlets, telephone outlet, fan regulator etc., shall be of  standard  factory  made  and  to  match  the  exact requirement of combination of outlets.  The boxes shall  be fabricated  out  of heavy gauge  CRCA  cold  rolled  carbon alloy sheet steel with zinc plating (G.I).   The size  of  boxes shall match the type  of  outlet/switch plate to be mounted on the box.  Adequate No. and  size of  knockout holes shall be provided to  terminate  the conduits in the box.  These boxes shall be of  standard  factory  made  product and of same make  as  of  switch plates  and sockets.  Separate screwed  earth  terminal shall be provided in the box for earthing.

             The  outlet  box  shall be of minimum  depth  of  50mm.Boxes  shall  be  suitable for grid  mounting  type  of accessories.  Long screw shall be provided to take care  of  the  extra plaster thickness to  mount  the  switch  plates.  Provision shall be made in the box and  switch  plate  to  have the minor adjustment  of  alignment  of switch plate to plumb level.

           SURFACE TYPE BOXES

            The  boxes  for mounting switches,  sockets  and  other  wiring devices shall be either moulded plastic or heavy gauge  CRCA sheet steel painted to match the colour  of  wall.   The  box  shall be suitable  to  terminate  the  G.I/M.S.  surface  conduit into the box. The  size  and  shape of box shall match the exact type and combination  of switch plates, receptacles and wiring devices.  Deep boxes  shall be used to facilitate easy termination  of conduit  and  wires/cables.   Separate  screwed   earth terminal shall be provided in the box for earthing. 

           LIGHT  OUTLET  BOXES  : 

            For  concealed  PVC   conduit  installation  the  light  outlet box shall  be  of  PVC  round/square with knock-out holes.  Conduit  projection  shall be suitable to terminate the conduit to the  box. The box shall be made of heavy gauge PVC and the sample to  have the approval of Construction  Manager   before  use.  The boxes shall have concealed screwed socket  to  fix the ceiling rose.   The boxes shall be minimum 50mm deep.

            For surface  conduit installation the light outlet  box  shall be of G.I/black enamelled M.S. boxes.  The  boxes shall  have  threaded stub projection  having  internal threading to terminate the conduits of different sizes.  The  boxes  shall  have concealed  screwed  socket  for  fixing  the  ceiling rose. The boxes shall  be  minimum 50mm deep.

            CEILING  FAN HOOK BOXES: 

            The ceiling fan hook  box shall   be  fabricated  of  2mm  thick  G.I/M.S.   with   adequately  sized G.I/M.S. rod/hook to fix the  ceiling fan.   The hook shall be concealed within the fan  hook box.  The side extensions of rod shall be  sufficiently  long to provide adequate anchorage in the concrete. The  size  of the box shall be such that it  should  be  totally  covered by the plastic canopy of  the  ceiling fan.  The box shall have anticorrosive primer coating.

            SWITCHES

            Switches  shall  conform to IS : 3854, and IS  :  4615. Switches  shall  be single pole, single or two  way  as shown  on  the drawings.  They shall be of  the  molded type  rated  for 250V, 5/15A.  They shall  be  provided with insulated dollies and covers. 

            The  switches  shall be rocker operated  with  a  quiet operating  mechanism  with  bounce-free,  snap   acting  mechanism  in an arc resistant chamber.   The  switches shall  have  pure silver and silver  cadmium  contacts.  The switches shall be of approved make as indicated  in  the  `List  of  Approved  Makes'.   Switches  installed  outdoors  shall  be industrial, metal  clad  type,  and shall be provided in weather-proof enclosure,  complete  with weather proof gasketed covers. 

             COVER PLATES FOR SWITCHES & OUTLETS

            Switches/sockets/wiring devices plates shall be of  the same make as of switches/sockets/wiring devices.  These shall be of best quality. Moulded plastic grid mounting  type device plates/frames shall be used and these shall  match with the type of switches/sockets and boxes. 

             COVER PLATES FOR INSPECTION/JUNCTION/PULL BOXES

             The cover plate for PVC boxes shall be with minimum 3mm thick perspex/formica sheet cover and for the  G.I/M.S. boxes,   shall  be of G.I/black enamelled  M.S.  plates. The  shape  of the plate shall match with that  of  the box.
           RECEPTACLES

            The  sockets  shall conform to IS  1293.   Each  socket shall  be provided with control switch  of  appropriate rating.   The sockets shall be moulded type  rated  for 250 volts and of 6 A or 16 A capacity as  mentioned  on the drawings.  The 16 Amps sockets shall be multi pin (6 pin) automatic shutter type suitable for plugging  6 A/16  A plugs.   The shutter shall open when  the earth pin of the plug is inserted in the socket.  Where called for, the 16 A socket shall have indicating lamp. The  socket  outlets  and switches  shall  be  of  grid mounting  type.   Where  called for  sockets  shall  be  provided with three pin plug top suitable to the socket  and  of  the same make as of socket.   The  plug  shall conform  to  IS  6538.  The  socket  outlets  installed  outside  the building/open to sky or in damp/wet  areas  shall of weather-proof, water-tight type.
           INDUSTRIAL TYPE SOCKETS

           The   socket  outlets  single  phase  or  three   phase installed  in electrical room,  D.G room etc., shall be three pin or 5 pin industrial  type with MCB (1 phase or 3 phase) control.  The socket  and  MCBs  shall be mounted in a sheet steel  enclosure  and shall be standard factory made product. 

           CONDUCTORS : 

            All PVC insulated copper conductor wires  shall  conform in all respects to standards  as  listed  under sub-head 'Regulations and Standards' and shall be  of 650/1100V Grade.

            PVC INSULATED WIRES (FOR LIGHT & SMALL POWER WIRING)

           The PVC cables shall conform to IS : 696/1977.  For all internal  wiring  PVC  insulated  cables  of  650/1100V  grade, single core shall be used.  The wires shall have  the approval of Tariff Advisory Committee.

The  conductors  shall  be  plain,  circular   stranded  annealed copper conductors complying with BS : 6360.

            The  minimum number and diameter of wires for  circular stranded conductor shall meet the requirements set  out in the relevant British Standards.

            The insulation shall be PVC compound complying with the  requirements  of BS : 6746.  It shall be applied by  an  extrusion process and shall form a compact  homogeneous  body.   The   PVC  compound  shall  comply   with   the         requirements of IS 5831-84.

           The cores of all cables shall be identified by  colours  in accordance with the following sequence.

                    Single phase           -    Red

                    Three phase            -    Red, Yellow, Blue

                    Neutral                    -    Black

                    Earth                       -    Green or Green/Yellow.

          A  means  of  identifying  the  manufacturer  shall  be provided throughout the length of cable. 

          Unless  otherwise specified in the drawings, the  sizes of  the cables/wires used for internal wiring shall  be as follows :

          In  case  of circuit wiring for lights,  exhaust  fans, ceiling fans, bells, convenience socket outlet points:-

               2.5 Sq.mm -  For Lights/fans/5A socket wiring  from  DB's upto the outlet points  including control   wiring  where  the   circuit length from the DB's to 1st outlet  is less than 40 m.

               In case of power socket outlet circuit. 

               6.0 Sq.mm -   From  DB's 20/32 A Industrial  type sockets.

               4.0 Sq.mm -    From  DBs to 16 A sockets.   

          The earth continuity conductor size as indicated in the  drawing/SOQ  shall be drawn through conduit along  with other  circuit  cables/wires.  The size  of  the  earth continuity conductor shall be as follows :-

          UNLESS  OTHERWISE  SPECIFIED  MINIMUM  SIZE  OF   EARTH CONTINUITY CONDUCTOR WIRES NOT FORMING PART OF THE SAME CABLE AS THE ASSOCIATED CIRCUIT CONDUCTOR.

	Nominal cross sectional area of largest associated copper circuit conductor in sq.mm
	Nominal cross sectional area of earth continuity conductor in sq.mm (PVC insulated green colour wire)

	1.5
	2.5

	2.5
	2.5

	4.0
	2.5

	6.0
	4.0

	10.0
	6.0

	16.0
	6.0

	25.0
	10.0

	35.0
	10.0

	50.0
	10.0


            Separate  circuits  shall run for  each  water  heater,  pantry/kitchen  equipment, window air conditioner,  and  similar outlets at locations as shown on drawings.

1.6     INSTALLATION OF CONDUIT

1.6.1  CONCEALED CONDUIT SYSTEM

           Unless  otherwise  Specified, all wiring  shall  be  in  heavy  gauge  rigid PVC conduit embedded  in  wall,  or ceiling and concealed in the false ceiling. The size of  the  conduit shall be selected in conformity with  I.S. code and as specified in the table given below. Factory made  conduit bends and accessories shall be used.  PVC Conduit shall be jointed using Solvent Cement as recommended  by  the conduit supplier. The  conduit  in ceiling  slab  shall be straight as  far  as  possible. Before  the  conduits  are laid  in  the  ceiling,  the  position of the outlet points, controls, junction boxes shall  be set out clearly as per the dimensions and  to minimise off-sets and bends.  Before the  reinforcement rods  are kept in position electrical contractor  shall mark in paint the position of outlet points and conduit  drop on the shuttering. When the outlet boxes are  kept in position and before pouring the concrete, all outlet  boxes  shall  be filled with paper to  avoid  entry  of  concrete  into  the box. Conduits in ceiling  shall  be  bonded to the reinforcement rods with G.I. bonding wire at  intervals not more than 1000mm, to secure  them  in  position.  PVC deep light outlet / pull boxes shall  be provided as required. The conduit in ceiling slab shall  be laid above the first layer of reinforcement rods  to avoid  cracks in the ceiling surface.   In general  the conduit  shall not be laid directly on  the  shuttering surface to avoid cracks in the ceiling surface.

           Conduits concealed in the wall shall be secured rigidly by  means  of  steel hooks / staples  at  min.  750  mm intervals.  Before conduit is concealed in  the  walls, all  chases,  grooves shall be neatly  made  to  proper required dimensions using electrically operated  groove cutting  tools to accommodate number of  conduits.  The  outlet boxes for control switches, inspection and  draw  boxes  shall  be fixed as and when conduits  are  being  fixed.  The recessing of conduits in walls shall be  so arranged as to allow atleast  12mm plaster cover on the  same.  All grooves, chases etc. shall be refilled  with  1:4 cement mortar and finished upto wall surface before plastering  of walls is taken up by the  general  civil  contractor.    Horizontal  chases  in  walls  are   not allowed.    Where  unavoidable,  prior  permission   of  owner/consultant  shall be obtained before  making  any chasing.  Where conduits pass through expansion  joints in  the building, adequate expansion fitting  or  other  approved  devices  shall be used to take  care  of  the relative movement. Whenever the conduits terminate into control boxes, distribution boards etc. conduits  shall  be   rigidly connected to the boxes/boards  with  check  nuts  on  either  side of the  entry.  After  conduits, junction   boxes,  outlet  boxes  etc.  are  fixed   in position, their outlets shall be properly plugged  with PVC  stoppers or any other suitable materials, so  that water, mortar, vermin or any other foreign materials do not  enter  into the conduit system. All  conduit  ends  terminating  into  an  outlet shall  be  provided  with bushes  of  PVC or rubber after the  conduit  ends  are  properly  filed  to  remove  burrs  and  sharp   edges. 

            Necessary  G.I. pull wires shall be inserted  into  the conduit for drawing wires before concreting.   Insulated  earth  wires shall be run  in  each  conduit originating from the panel board upto the Light, Socket  and Switch boxes.  If the Electrical Contractor forgets to install any conduit/boxes etc., before the  plastering/painting work is done by other agencies, he may  be permitted to install the same with prior permission  of  owners/ consultant and he shall be liable to make  good  the wall, floor, ceiling etc. at his own cost.

            Conduits  shall  be so arranged as to  facilitate  easy  drawing  of wires through them.  Entire conduit  layout shall  be  done in such a way as  to  avoid  additional  junction  boxes  other than light points.   The  wiring  shall  be  done in a looping manner.  All  the  looping  shall  be done in either switch boxes or outlet  boxes.  Joints  in  junction  or pull boxes  are  strictly  not  allowed.   Where  conduits  cross  building   expansion  joints,  adequate expansion fittings or other  approved devices  shall  be used to take care  of  any  relative  movement. 

All conduits shall be installed so as to avoid touching   of steam and hot water                                              pipes. 

            Conduits  shall  be installed in such a  way  that  the junction and pull boxes shall always be accessible  for repairs   and  maintenance  work.   The   location   of junction/pull  boxes  shall  be  marked  on  the   shop drawings and approved by the owner/consultant.

            A  minimum  separation  of 200mm  shall  be  maintained between electrical conduits and hot water lines in  the building. 

            No  run  of  conduit shall exceed  ten  meters  between adjacent draw-in points nor shall it contain more  than two  right  angle bends, or other  deviation  from  the  straight line. 

             Caution shall be exercised in using the PVC conduits in locations  where  ambient  temperature  is  50   degree celsius or above.  Use of PVC conduits in places  where ambient  temperature  is  more  than  60  degree  C  is  prohibited.  The entire conduit system including  boxes  shall   be  thoroughly  cleaned  after  completion   of installations  and  before drawing of  wires.   Conduit system shall be erect and straight as far as  possible.  Traps where water may accumulate from condensation  are to  be avoided and if unavoidable,  suitable  provision for draining the water shall be made.

            All  jointing methods shall be subject to the  approval  of the owner/consultant.

            Separate  conduits shall be provided for the  following  system. 

 - Lighting wiring

               - 16 Amp power outlets.

               - 6 Amp outlets and lighting system.

               - 24 Volt supply system.

               - Telephone/intercom system,

               - Fire Alarm system,

               - Computer data cabling system.

               - Equipment wiring. 

            CONDUIT JOINTS
            Conduits  shall be joined by means of  plain  couplers.  Where  there  are  long  runs  of  straight   conduits, pull/inspection  boxes shall be provided at  intervals, as  approved  by  the  owner/consultant/construction manager.   The  conduits shall be thoroughly cleaned before making  the joints.   In  case  of  plain  coupler  joints,  proper  jointing material like a vinyl solvent cement (gray  in color)   or   any  material  as  recommended   by   the manufacturer shall be used. 

            BENDS IN CONDUIT
            Wherever  necessary,  long bends or diversions  may  be achieved by bending the conduits or by employing normal bends.  No bends shall have radius less than 2.5  times  outside  diameter of the conduit.  Heat may be used  to soften the PVC conduit for bending, but while  applying   heat  to the conduit, the conduit shall be filled  with sand  to avoid any damage to the conduit. Kinks in  the conduit bends shall not be acceptable.

            BUNCHING OF CABLES
            Cables  of  AC  supply of  different  phases  shall  be  bunched in separate conduits.  The number of  insulated wires/cables that may be drawn into the conduits  shall be  as  per the following table.  In  this  table,  the  space factor does not exceed 40%.  However, in any case conduits  having less than 20mm diameter shall  not  be used. 

             MAXIMUM  PERMISSIBLE  NUMBER OF 650 VOLT  GRADE  SINGLE CORE WIRES  THAT MAY BE DRAWN IN TO RIGID PVC CONDUITS.

	CABLE SIZE IN Sqmm
	SIZE OF CONDUITS (mm) (MAX NO. OF WIRES)

	
	20
	25
	32
	40
	50

	
	
	
	
	
	

	1.5
	4
	8
	14
	-
	-

	2.5
	4
	6
	10
	-
	-

	4.0
	3
	4
	8
	12
	-

	6.0
	2
	4
	6
	8
	-

	10.0
	1
	3
	5
	10
	-

	16.0
	0
	2
	4
	5
	12


           Wires  carrying  current  shall be so  bunched  in  the conduit  that the outgoing and return wires  are  drawn into  the  same conduit.  Wires  originating  from  two different phases shall not be run in the same conduit. 
          WIRING :

             All   final  branch  circuits  for  lighting   and appliances, shall be single conductor cables run inside conduits.   Branch circuit conductor sizes shall  be  as shown in the load analysis of drawing and conforming to the requirements of the I.E. Regulations and I.S. Code.

            Home  runs  indicated  on the drawings  for  the  final branch  circuits  shall be kept in a  separate  conduit  upto the panel board via switches wherever called  for. No  other  wiring  shall be  bunched   in  the  conduit  unless the other circuit main of same phase runs in the same conduit.

             For each lot of wire supply, Contractor shall supply a certificate  issued  by the  Manufacturer  stating  its origin, date of manufacture, constitution and standards  to which it complies and the test certificates. 

             Looping system of wiring shall be used. Wires shall not be  jointed  inside the conduit or pull  boxes.   Where joints  are  unavoidable, they shall  be  made  through approved mechanical connectors with prior permission of owner/consultant. 

            Control  switches  shall  be  connected  in  the  phase conductors  only and shall be 'ON' when knob  is  down. Switches  shall  be fixed in  galvanised  steel  boxes. Chromium plated screws shall be used. 

            Power wiring shall be distinctly separate from lighting wiring.

            Each  circuit phase wire from the  distribution  boards should be followed with a separate neutral wire of  the same size as the circuit wire. 

             BUNCHING OF WIRES :

            Wires carrying current shall be bunched so that the outgoing  and  the  return wires are  drawn  in  the  same conduit.  Wires originating from two  different  phases shall not run in the same conduit. 

             DRAWING  CONDUCTORS :  

            The drawing and jointing  of PVC  insulated copper conductor wires and cables  shall  be   executed   with  due  regard  to   the   following  precautions.   While  drawing wires  through  conduits, care shall be taken to avoid scratches and kinks  which cause  breakage of conductors. There shall be no  sharp bends.

            Insulation  shall  be shaved off like sharpening  of  a  pencil  and  it  shall not be  removed  by  cutting      it square.

            PVC  insulated  copper  conductor wire  ends  shall  be soldered (atleast 20 mm length).

            Strands  of  wires  shall  not be  cut  for  connecting  terminals.   The terminals shall have sufficient  cross sectional  area  to  take  all  strands  and  shall  be soldered.   Connecting  brass screws  shall  have  flat ends.    All  looped  joints  shall  be  soldered   and  connected   through  block/connectors.   The   pressure applied  to  tighten  terminal  screws  shall  be  just  adequate, neither too much nor too less.  Conductors of  all  sizes  shall  always  be  terminated  using  cable sockets.   At all bolted terminals, brass flat  washers of  large area and approved steel spring washers  shall be  used.  Brass nuts and bolts shall be used  for  all connections.

            Only  certified  wiremen and cable  jointers  shall  be employed  to  do jointing work.  All wires  and  cables  shall  bear  the  manufacturer's  label  and  shall  be brought to site in original packing.  For all  internal  wiring,  PVC  insulated wires of 650/1100  volts  grade shall be used.  The sub-circuit wiring for point  shall be  carried out in loop system and no joints  shall  be allowed in the length of the conductors.  If the use of  joint  connections are unavoidable due to any  specific reason, prior permission, in writing, shall be obtained from the owner/consultant.  No wire shall be drawn into any  conduit,  until all work of any nature,  that  may cause  injury  to wire, is completed.   Care  shall  be taken in pulling the wires so that no damage occurs  to the insulation of wire. Before the wires are drawn into  the conduits, the conduits shall be thoroughly  cleaned of  moisture,  dust, dirt or any other  obstruction  by forcing  compressed  air  through  the  conduits.   The minimum  size of PVC insulated conductor wires for  all  sub-circuit wiring for light points shall be 2.5 sq.mm.
   JOINTS  :  

            All joints shall be made at main  switches, distribution  boards, socket outlets, lighting  outlets and  switch boxes only.  No joints shall be  made  in  conduits  and in junction boxes.  Conductors  shall  be continuous from outlet to outlet.

             MAINS  AND SUB-MAINS :  

             Mains and sub-mains cables  or  wires  where called for shall be of the rated  capacity  and approved make.  Every main and sub-main wire  shall be drawn through an independent adequate  size conduit. An independent earth wire of the proper rating shall be provided for every single phase submain.  For every  3-phase  submain,  2 nos. earth wires  of  proper  rating  shall  be  provided alongwith the submain.   The  earth  wires shall be drawn inside the conduits along with the circuit  main.  Where mains and sub-mains   cables  are connected to switchgear, sufficient extra lengths  of  cables shall be provided to facilitate easy connections and maintenance.

            LOAD  BALANCING : 

            Load balancing of circuits  in  three phase   installation  shall  be  planned   before   the commencement  of wiring and shall be  strictly  adhered to.

            COLOUR  CODE  OF  CONDUCTORS :  

            Colour  code  shall  be maintained  for  the entire wiring  installation:  red, yellow,  blue  for  three phases,  black  for  neutral, green/yellow green for earthing.

            The  control  wire from light control switches  to  the  light/fan  points shall be the same colour as  that  of  the phase/circuit wires feeding that particular loop.
            EARTHING

            All earthing system shall be in accordance with IS 3043 - 1985 Code of practice for Earthing. 

           The  type  and  size  of  earthing  wire  shall  be  as specified under the heading of cables. 

           Each conduit originating from the DB to various outlets shall  have one earth wire (PVC insulated green  colour wire).
           TESTING OF INSTALLATION
           Before  a completed installation is put  into  service, the following tests shall be complied with :

           INSULATION RESISTANCE

           The insulation resistance shall be measured by applying  500 Volt  megger  with all  fuses  in  place,  circuit  breaker and all switches closed. 

           The insulation resistance in megohms of an installation measured  shall not be less than 50 megohms divided  by the number of points in the circuit.

          The insulation resistance shall be measured between

               Earth   to   Phase

               Earth   to   Neutral

               Phase  to    Neutral

          EARTH CONTINUITY PATH

            The  earth  continuity conductors shall be  tested  for electrical continuity and the electrical resistance  of the same along with the earthing lead but excluding any added  resistance  or  earth  leakage  circuit-breaker, measured from the connection, with the earth  electrode to  any point in the earth continuity conductor in  the completed installation and shall not exceed one ohm.

          POLARITY OF SINGLE POLE SWITCHES

            A  test shall be made to verify that every  non-linked, single pole switch is connected to one of the phases of  the supply system. 

          COMPLETION CERTIFICATES

            All the above tests shall be carried out in presence of  Construction Manager and the results shall be  recorded  in  prescribed forms.  Any default during  the  testing  shall be immediately rectified and that section of  the  installation  shall  be retested.  The  completed  test  result   forms  shall  be  submitted  to   the   owner/consultant.
            On completion of an electric installation a certificate shall be furnished by the contractor, countersigned  by the certified supervisor under whose direct supervision the  installation  was carried out.   This  certificate shall be in a prescribed form as required by the  local electric supply authority. 
           MEASUREMENTS
           Mode of measurment is as follows :
For  purposes of measurment the point  wiring  for lights/fans/6A  sockets  (where  6A  sockets   are connected  to  lighting circuit loop)  is  divided  into two parts.
a) Point Wiring
              b)    Circuit Main
          a)   POINT WIRING
          The  wiring  for  light/fan/6A  socket  (where  6A  sockets  are connected to lighting  circuit  loop) point  starting  from first  light/switch/fan  and looping between switches/ fans/sockets etc., shall be measured either in `Number' or `Set'.

          One light/fan point controlled by one  switch  is  measured in Number (No.)
          Set of Two or more light points controlled by  one switch is measured in `Sets'.

          Where  set of light points wired  and  controlled directly from MCB DB shall be measured in `Sets'.  The rate for this item shall not include the cost of switch & switch box. 

          6A socket wiring where connected to the  lighting circuit loop is measured in Number (No.)

          b)    CIRCUIT MAIN
          The  length of circuit main including conduit  starting   from MCB DB to first switch/light/fan shall be measured separately  in `Linear Metres' (Rm). (Futher wiring  is measured in point wiring).

          CIRCUIT  MAIN  FOR WIRING 6A  SOCKETS,16A  SOCKETS  AND  POWER OUTLETS SHALL BE MEASURED AS UNDER
          Length of circuit wire including conduit  starting from  MCB  DB to outlets and  looping  between  outlets shall be measured in linear metres (Rm). 

          The commercial type socket outlet with outlet box and  cover plate shall be measured in numbers (No.)
          The Industrial type socket outlet including MCB, plug top,  outlet box and cover plate shall be  measured  in numbers (No.)

          The plug tops where called for shall be measured  in  numbers (No.)

B.
M.V.DISTRIBUTION BOARDS

SCOPE :

           This section covers the design, manufacture,  assembly, testing  at manufacturer's works,  inspection,  packing           for  transportation,  delivery at  site,  installation, connection,  testing and commissioning of  415V  switch boards  with guarantee of performance for a  period  of  twelve (12) months from the date of commissioning.  The contractor   shall  provide  all   materials,   labour, equipment,  scaffolding  etc.,  as  required  for   the completion of the job. 

STANDARDS APPLICABLE

The following standards and rules shall be applicable :

The  Distribution Boards shall comply with  the  latest edition   of  relevant  Indian  Standards  and   IndianElectricity  rules  and  regulations.   The   following Indian Standards shall be complied with :

IS 4237-83  General requirements for switch gear and control gear for voltages not  exceeding 1000V.

IS 5578-85     Guide    for   marking   of    insulated conductors.

IS 11353-85 Guide for uniform system of marking  and identification    of   conductors and  apparatus terminals.

IS 2147-62     Degree of protection provided by enclosures  for low voltage switch  gear and control gear.

IS 2675-83     Enclosed  distribution fuse  boards  and cutouts   for  voltages  not   exceeding 1000V.

IS 2551-82     Danger notice plates.

IS 2516        Circuit  breakers Part 1.   Requirements (Part I/Sec 1):and  tests  : Section 1.   Voltages  not  exceeding 1000V ac or 1200V dc.

IS 4064-78    Air    break   switches,    air    break disconnectors,    air    break    switch disconnectors and fuse combination units  for  voltages not exceeding 1000V ac  or 1200V dc.

IS 1818-72     Alternating      current       isolators (disconnectors) and earthing switches.

IS 8623-77 Factory  built assemblies of  switchgear and  control  gear for voltages upto  and  including 1000V AC & 1200V DC.

IS 8828-78     Miniature air break circuit breakers for voltages not exceeding 1000V.

IS 9926-81     Fuse  wires  used  in  rewireable   type electric fuses upto 650 Volts.

IS 8544-79     Motor   starters   for   voltages    not  exceeding  1000 Volt A.C. or  1200  Volt  D.C.

IS 2959-85     Contactors  for voltages  not  exceeding 1000 Volt A.C or 1200 Volts D.C

IS 9224-79     Low Voltage fuses.

IS 12640-89    Residual   current   operated    circuit  breakers.

IS 1248-83   Direct   acting   indicating    analogue  (all parts)    electrical  measuring  instruments   and                            their accessories.

IS 2705-81     Current transformers. (all parts)

IS 4201-83     Application     guide    for     voltage transformers.

IS 8197-76     Terminal    markings  for  electrical measuring  instruments    and    their accessories. 

 Indian Electricity Act and Rules.

 415V SWITCH BOARDS

The  415  volt switchboard shall be  metal-clad,  dead front totally enclosed, indoor type, forming a  self  supporting continuous board.  The front portion of  the  board shall have individual compartments  arranged in  tier  formation to accommodate draw-out  type  air-circuit-breakers.  The back portion of the board  shall  contain three-phase and neutral  air-insulated busbars,  cable terminations, instrument transformers, etc.   The  busbars and all other outgoing live terminals shall  be protected to prevent accidental contact while  carrying out maintenance work.

DISTRIBUTION ARRANGEMENT

For  single transformer load-centres, the  panel  shall accommodate  one transformer secondary  circuit-breaker           and  specified number of outgoing circuit-breakers  all connected to the common busbar.

For  two  transformer load-center,  the  415  volt  bus shall be sectionalised and  each  transformer shall  be  connected to the  corresponding  bus-section over  its secondary circuit-breakers.  Bus-tie  circuit  breaker shall be provided between adjacent bus sections and  the outgoing switchgear distribution on each  bus-section shall be as specified.

415 VOLT MAIN BUSBARS

Copper / Aluminium bus-bars shall be used. Busbars shall be made from rectangular sections of high wrought aluminium alloy and the current density shall not exceed 0.8 A / sq.mm and where copper sections are used the current density shall not exceed 1.4 A / sq.mm. 

The  continuous  current rating and the  short  circuit values  which  the main busbars are able  to  withstand          shall be as follows :-

	TRANSFORMER RATING
	CONTINUOUS CURRENT RATING
	SHORT CIRCUIT CURRENT RMS SYMMERICAL

	Kva
	A
	A

	400
	630
	15000

	750
	1250
	21600

	1000
	1600
	36000

	1600
	2500
	36000

	2000
	3200
	50000


 The  neutral bus bars shall be designed to carry 50  percent continuous current rating of the main busbars.

 415 VOLT CIRCUIT-BREAKERS

The  circuit-breakers shall be  triple-pole,  air-break draw-out  type.  All current carrying contacts  of  the         breakers  shall be silver plated.  Arc-chute fitted  on each  pole shall be easily removable for inspection  of   the  main  contacts.  Inter-phase  barriers  of  proper design shall also be incorporated.

The  plug  connections of main  and  auxiliary  circuit  shall   be fitted with self-aligning  contacts.  The  fixed  position of the plug  connections  shall  be easily   accessible  for  maintenance.    Automatically  operated shutters shall be provided to screen the fixed portion  of  the  plug  when  the  breaker   is   fully  withdrawn from the cubicle.

The continuous current ratings of the various  Circuit-Breaker   units at specified ambient temperature  shall           be as specified.  The RMS Symmetrical breaking capacity  of  the  different  air circuit-breakers  shall  be  as           follows, unless otherwise specified :-

	CURRENT RATING OF THE ACBs
	BREAKING CAPACITY RMS SYMMETRICAL AT PF OF 0.2 TO 0.3

	A
	A

	
	

	200
	15000

	400
	21000

	630
	36000

	1000
	36000

	1600
	36000

	2500
	36000

	3200
	50000


OPERATING MECHANISM

The  Circuit-breakers  shall  be  either  manually   or electrically  operated  as  specified.   For  emergency         closing and testing, the electrically operated  breaker shall  be  capable  of manual  closing.   For  manually          operated  breakers,  manual,  independent-type  closing  mechanism  shall  be  provided.   If  manual  dependent      mechanism   is   provided  then  the   breakers   shall  compulsorily  have  electrical  closing  and   tripping   devices.   All types of operating mechanisms  shall  be trip-free throughout the breaker travel and designed to reduce mechanical shock to a minimum during  operation. All electrically  operated  breakers shall be  provided with mechanical/electrical anti-pumping device.

Each  breakers shall be equipped with visible 'ON'  and   'OFF'  position  indicator  on the front  door  of  the           compartment,  mechanically  connected to  the  circuit- breaker   mechanism.   Separate ON and  OFF  indicating lamps also shall be provided.

For     electrically     operated     circuit-breakers, satisfactory  operation shall be guaranteed for closing   the circuit-breakers  with   the   operating  voltage  of  the drive, in the range of 85 to  110  percent   of  the rated voltage.  The  electrical  closing  shall  be  either by solenoid or motor  operated  spring charged mechanism suitable for 240 V AC.

The  circuit-breaker   shunt trip coil  provided  shall operate   satisfactorily  with  the  operating  voltage         within  the  range of 70 t0 120 per cent of  the  rated  voltage.   The shunt trip  coil shall be  suitable  for 240 V AC.  No separate control source will be available as such capacitor trip Circuit shall be provided  where shunt  tripping  is proposed with protective  relay  so that ability to trip is not impaired by momentary  drop  in voltage at the time of a fault.

Each  circuit-breaker shall be provided with four  (4)  normally  open  and  four  (4)  normally  closed  spare           auxiliary  contacts  in addition to  the  ones  already used  for  various  control  purposes.   All  auxiliary  contacts  shall be wired internally up to the  terminal block.

INTERLOCKS

           The  switchgear  shall be provided with  all  necessary interlocks designed to prevent incorrect operation  and to  ensure safety of operating personnel and  also  the equipment.

The moving  portion of the circuit-breakers shall be  so interlocked that with the breaker  closed it shall  not be  possible to isolate it from the connected  position or to plug it in from the isolated position.

Interlocking shall be provided to prevent operation  of the  circuit-breaker unless it  is  fully plugged in or  fully  isolated  and  is  locked  correctly  in  either position.

The  circuit-breaker  compartment  doors  shall  be  so interlocked as to prevent access to a breaker which  is  in an energized and plugged in position.  Special  means shall however be provided for undoing this interlock in an emergency.

Inadvertent  withdrawal  of a  circuit-breaker  movable unit  too  far beyond its  supports  shall  be prevented by a suitable mechanical stop.

The  unit  shall be provided with  "test"  position  in  which the circuit-breaker main contacts  are in  the  fully  disconnected  position  with  only  the secondary circuits remaining connected.  All secondary connections including control, signaling and  metering circuits between the fixed and removable sections shall  be  by  means  of flexible able and  plug  and  socket arrangement.

PROTECTIVE DEVICES

The  circuit-breakers  shall be provided on  each  pole  with  any   combination  of   the   following protective  devices with ratings as called for  in  the specification:

         i)  Direct  acting over current tripping device with  long  time    element   having   inverse    time    current           characteristic  for protection against overloads  and instantaneous element for short-circuit tripping with   alarm contact.

        ii)  Direct  acting over current tripping device with  long  time    element   having   inverse    time    current           characteristic  for protection against overloads  and short  time  element  with definite  time  delay  for short-circuit protection with alarm contact.

      iii)  Shunt tripping device with alarm contact.

      iv)   Non-directional IDMT earth fault relay.

       v)  The under voltage tripping device when specified shall be designed for the following operating conditions:

            a) The circuit-breakers shall trip for voltage value set between 70 and 35 per cent of  rated  system                 voltage.

            b)  The  under voltage relay shall not prevent  manual closing  of the circuit-breaker  above  85 percent of rated system voltage.

      vi)  The  CTs provided for  protective devices  shall  have adequate VA capacity and accuracy class of 10P10.

INSTRUMENTS AND METERS

Instruments,  meters  and  relays shall  be  of  flush-mounted design, housed in dust-proof casing located  in an  accessible  position  on the  breaker  panel.   All incoming circuit-breaker units shall be provided with a voltmeter  and changeover switch on the live  side  for indicating the three-phase voltages and ammeter with  a changeover switch complete with C.Ts for measuring  the currents  in all three phases.  Ammeters with C.Ts  and selector  switches  shall  also  be  provided  for  all outgoing feeders.  For motor feeders the ammeter  shall  be  provided with a normal scale up to full-load  value and a suppressed scale beyond full-load for  indication of  motor starting current.  C.Ts provided for  ammeter shall have accuracy Class of 1.0 KWH meters, 15-minute maximum demand indicators shall be provided, where specified.
CABLE TERMINALS

The  cable terminal arrangement for incoming  415  volt circuit-breaker from 400 KVA transformer secondary  and for all outgoing feeders shall be suitable for  single-core  and multi-core aluminium conductor  PVC  insulated  cables  of number, type  and sizes as  specified.   The termination arrangement of multiple cables shall permit connection and disconnection  of each individual  cable  without  disturbing the other cables.  For  termination  of  cables  suitable  lugs  of  proper  size  shall  be  provided.   Where armoured cables are to be  terminated suitable armour clamps shall be provided.

LOW VOLTAGE BUS-DUCTS

Bus-ducts  with  3 phase and neutral busbars  shall  be able  to  withstand  the  short-circuit   currents   as  specified  in item 1.04  above.  It shall  be  designed for a rated voltage of 1,000 volts.

The  bus-duct  shall  be of  metal-enclosed,  dust  and vermin proof  type  divided into factory  made  sections suitable  for  easy  assembly at  site.   It  shall  be complete  with mounting arrangement and  all  necessary accessories required to make the installation complete.

The  bus-duct  shall have suitable  side  covers  where required  for  easy access to all the  busbars.   Space shall  be  provided  within  the  bus-duct  for  taking secondary wiring as required,  The bus-bar supports and  their terminal connections shall be designed to  permit expansion  and contraction of the bar with a  variation in  the site ambient temperatures.   Throat  connection with links shall be provided at the transformer terminal for easy removal of transformer, when necessary. 

ALARM AND INDICATION

Each  load-centre  substation shall  be  provided  with static audible and visible alarm indication with  alarm accept and cancellation device.  The system shall  have arrangement  for  repeat alarm facilities as  well  as testing  the  alarm  circuits.   The  scheme  shall  be designed to give the following indications:
         i) When any circuit-breaker trips on fault only

        ii) Temperature rise of winding

       iii) Earth fault indication

Provision  shall  be made for transmitting  signals  if required  to  remotely  located  signaling  system  to  indicate tripping of incoming circuit-breaker on  fault and  operation  of earth fault relay  provided  in  the transformer  neutral circuit. Provision shall  also  be  made  to transmit the alarm and tripping signals to  33 kV switchboard from  which the transformer is fed or to a remote signaling panel.

REMOTE CONTROL SCHEME FOR BREAKERS

For electrically operated circuit-breakers in  addition to ON-OFF control switch provided on the front side  of  the panel, provision shall  be made where required  for remote closing and tripping of circuit-breakers from an external  control  desk  with  arrangement  to  prevent closing of the breaker by the control switch mounted on  the front of the circuit-breaker cubicle.

OTHER CONSTRUCTIONAL FEATURES

All operating handles, control switches,  push-buttons, indicating  lamps,  instruments, meters  etc  shall  be mounted on the front of the cubicles.

The auxiliary relays for temperature alarm and tripping shall  be  mounted  on  the  incoming  breaker  panels.           Terminal  boards shall be provided at  the  transformer sections  for  all control circuit taken out  from  the transformers.  All wiring from these terminal boards to the  switchgear  sections shall be  provided  with  the         equipment.

All  wiring  within  the cubicles  shall  be  with  PVC insulated  cables  and shall be  effectively  protected   from  possible damage by electrical flashover.  As  far as  possible  each essential control circuit  shall  be contained in the respective cubicle.  All wiring  shall be  such that it is easily identifiable and  accessible for maintenance.

For  equipment earthing a suitable copper earthing  bus shall  be  provided  for the complete   length  of  the switch board and bonded to all the units including  the transformer   and   high  tension   cubicles.    Proper terminals shall  be  provided  for   external   earth connections to be fully in conformity with IER.

A suitable universal type truck shall be provided  with each   load-centre  substation  for   withdrawing   the     breakers  from  the  board.   The  trucks  shall   have platforms  of adequate mechanical strength for  bearing  the  weight of the circuit-breaker units and  shall  be provided  with  necessary guide rails and  stops.   The height of the platform shall be adjustable to suit  the levels  at  which the  different  circuit-breakers  are mounted on the switchboard.

Identification  labels  shall  be  provided  for   each circuit-breaker  and control devices to be  located  in readily  visible positions.

All  steelwork  of each  load-center  substation  shall  undergo  rust removal procedure before  application  of  primer  and  shall  be  given  epoxy  paint  finish  of Aircraft Grey colour as per ISS Shade 693 or any  other colour of approved shade.

The busbars of each unit substation shall be painted as per following norms:

              A Phase            -  Red

              B Phase            -  Yellow

              C Phase            -  Blue

              Insulated neutral  -  White

              Earthed neutral    -  Black

ABC  are  the  three phases of AC  circuit   with  anti-clockwise vector rotation.

 TEST
All  equipment shall be tested in accordance  with  the relevant clauses of applicable standards.  All  internal  wiring  shall be checked for correct  operation  before dispatch.    
C       M.V. CABLES  AND CABLE TRAYS         
           SCOPE OF WORK :

           This  section covers the supply, installation  storing, laying,  fixing,  jointing / termination,  testing  and      commissioning  of Medium Voltage PVC insulated or  XLPE  insulated  PVC  Sheathed  armoured  aluminium/   copper conductor  cables laid in built up  trenches,  directly buried  underground, on cable trays, in pipes,  clamped  directly  to wall or structures etc. as called  for  in  the   drawing.   The  contractor  shall   provide   all     materials,  labour, equipments, scaffoldings  etc.,  as required for the completion of M.V. Cables, Cable Trays etc., as called for.

          STANDARDS APPLICABLE

          The following standards and rules shall be applicable. 

IS 1554-88  PVC insulated (heavy duty) electric  cables Part I for working voltages upto and including 1100V. 

          IS 8130-84  Conductors  for insulated  electric  cables and flexible cords.

          IS 3961-67  Recommended current ratings for cables: (Part  2):  PVC  insulated and PVC sheathed heavy  duty                        cables.

          IS 5831-84  PVC  insulation  and  sheath  of   electric cables.

          IS 7098-89  Cross linked polyethylene insulated PVC sheathed cables.

       The individual cores shall have continuous numbering of  the core all along its length and also be provided with identification  ferrules  at  both  ends.    Individual control cables shall have 20% spare cores.

          FRLS  cables shall be used for fire  protection  system controls to prevent flame propagation, smoke  reduction         and to avoid toxic gas emission in the event of a fire.  FRLS  compound  shall be tested rigorously  for  oxygen         index  as  per ASTM D2863, acid gas generation  to  IEC 754-1, smoke density to ASTM D 2843 and flammability to  SS 424 1475 class F3, IEEE 383 and IEC 332-1.

          Manufacturer's  name,  ISI Mark, cable  size  and  type shall  be clearly embossed at regular intervals on  all    cables. 

         TYPE AND QUALITY

            Medium  voltage  cables shall  be  circular,  multicore annealed copper or aluminium conductor, PVC  insulated,         PVC  sheathed  and steel wire armoured  or  steel  tape armoured  construction or unarmoured..  The  conductors of  cable  shall be stranded.  Sector  shaped  stranded conductors  shall be used for cables of 50  sq.mm  size and above.  The cables shall conform to IS:1554  part-I in all respects.

            M.V  power cables shall have 3, 3.5 or 4  cores,  as required and shall have conductors made from electrical  purity  aluminium conductors conforming to IS : 8130  - 84.

            Conductors  shall  be insulated with high  quality  PVC base   compound.    Insulation  and   outer   sheathing  compounds shall conform to IS 5831 - 84.

            A  common  covering shall be applied over  the  laid-up cores  by  an extruded sheath of  un-vulcanised  rubber       compound.

            Armouring of galvanised round steel wires or galvanised  flat  steel  strips shall be provided  over  the  inner sheath.

Outer  sheath  of  PVC  shall  be  extruded  over   the armouring.  Cables shall be manufactured and tested  in       accordance with IS 1554.

            Unless otherwise specified, all control cables shall be multicore,  1100V  grade PVC  insulated,  armoured  and          overall PVC sheathed with stranded copper conductors of 2.5  sq.mm,  conforming  to IS  1554.  Cores  shall  be           identified by colour scheme of PVC insulation. 

RATING :

The  cables  shall be rated for a voltage  of  650/1100 Volts.

Core Identifications :

            Cores  shall  be  provided with  the  following  colour scheme of PVC insulation :

          1.   Single Core    :    Green yellow for earthing.

          2.   Two Cores      :    Red and Black, Blue & Black, Yellow & Black.

          3.   Three Cores    :    Red, Yellow & Blue 

          4.   Four Core      :    Red, Yellow, Blue & Black

          INSPECTION  : All cables shall be tested  inspected  at manufacturer's  works.   However upon receipt  at  site  cables shall  be checked for physical  damages  during  transit.

JOINTS IN CABLES :   The contractor shall take care  to see   that   all  the  cables  received  at  site   areapportioned to various locations in such a manner as to ensure  maximum utilisation and avoidance  of  straight  cable  jointing.   This   apportioning   shall  be  got approved by the Construction Manager. before the cables are cut to lengths.

Where straight joints in cable are unavoidable, the use and  location  of  such straight joints  shall  be  got  approved by Construction Manager.

JOINTING BOXES FOR CABLES :  Cable joint boxes shall be of  appropriate  size,   suitable  for  PVC   insulated armoured cables of particular voltage rating.

JOINTING  CABLES :  All  cable joints shall be made  in suitable,  approved  cable  joint  boxes,  jointing  of  cables  in  the  joint  boxes and  the  filling  in  of  compound    shall   be   done   in   accordance    with manufacturer's instructions and in an approved  manner.  All straight joints shall be done in epoxy mould  boxes  with  epoxy resin only of makes/types as  indicated  in  the  list  of  approved makes. All  terminal  leads  of conductors  shall be heavy soldered upto at least  50mm length. 

All cables shall be joined colour to colour and  tested for   continuity  and  insulation   resistance   before jointing  commences. The seals of cables shall  not  be  removed until preparations for jointing are  completed. Joints  shall be finished on the same day as  commenced and  sufficient  protection from the weather  shall  be arranged.    The   conductors  shall   be   efficiently insulated  with  high voltage insulating  tape  and  by  using  preaders  of approved size  and  pattern.   The joints  shall be completely filled with epoxy  compound and  taped  so as to ensure that the  box  is  properly filled.


Epoxy compound shall be filled as follows :

Equal quantities of resin and hardener shall be mixed thoroughly by hand until the mixture is free from white patches and has uniform colour.  No water, oil or any other liquid shall be added to the mixture to make it soft as is will affect the properties of   the compound.   The mixture shall be used within 30-40 minutes of mixing.  The on which epoxy compound is to be used, shall be free from dust, rust, oil, grease and shall be dry.  The joint neither be disturbed   nor moved till the epoxy compound   is completely hardened.  A smooth surface can be made by rubbing a damp cloth smoothly on the compound before it sets.   The  joints shall be painted  after  they  have      completely hardened. 

Alternatively, ready mix of epoxy cable   jointing compound may also be used. In all cases manufacturers recommendations shall be strictly adhered to .

          CABLE  MARKERS

            All underground cables and cable joints shall be marked on  the surface by markers generally  manufactured  and          tested to the requirements of relevant Bureau of Indian Standards. Approved CI cable markers shall be  provided        at every 30m along the route of the cables and at  both ends  of  road crossing, indicating  cable  joints  and  cables  as  applicable.  Special CI  markers  shall  be provided   at  all  buried  cable   joints   indicating "Electrical  Cable  Joints".  CI plates  duly  engraved with  the  size of the cable and the  place  it  serves shall  be tied to the cable at regular intervals of  5m for easy identification of cables.

TERMINATION OF CABLES
Cable  termination  shall be done in  terminal  box  or cable    end   box   or   distribution    boards,    or     apparatus/ equipments.  Terminations are to be made with mechanical  and glands be tinned/nickel  plated,  anti      corrosive,  three  piece improved pattern which  is  to grip inner and outer PVC sheaths as well as the  armour of the cable.  The cable ends or the core conductor are to  be  connected by solderless lugs or  sockets  using  crimping tool of approved make for all cables. 

All   terminations   of  cable  conductors   and   base conductors shall be mechanically and electrically sound and   shall  comply  with  the  requirements   of   IEE  regulations. 

The  connectors or connecting sockets are to have  such dimensions so as to limit temperature rise. 

When required the water tightness of the terminal boxes may  be obtained by filling with a compound  preferably plastic  flame-retarding and non-dripping  type  within  the normal range of temperatures.

            When the cable is cut during the course of installation the open ends are to be sealed immediately by means  of  self-adhesive  non-hygroscopic tape over a  wax  water seal to make an air and watertight joint.

          INSTALLATION OF CABLES

          Cable  shall  be laid in a manner as indicated  on  the drawings.   Generally cables are laid in the  following  manner.

            i. In the underground masonry trench.

           ii. On the cable tray/or on cable ladders.

          iii. Buried underground.

           iv. Through pipe sleeves.

          Various  installation  methods  are  discussed  in  the following paragraphs. 

          Cables shall be laid by skilled and experienced workmen using  adequate rollers to minimize stretching  of  the cable.  The cable drums shall be placed on jacks before unwinding the cable.  The cable drums shall be  rotated in  the  direction as indicated  by  the  manufacturer.  Care  shall  be  exercised in laying  cables  to  avoid  forming kinks.  The drums shall be unrolled and  cables run  over  wooden  rollers,  placed  at  intervals  not  exceeding two (2) meters. 

GENERAL

All  cables shall be adequately protected  against  any  risk  of mechanical damage to which they may be  liable in normal conditions of service. 

When   cables  pass  through  holes  in   metal   work,  precautions  shall be taken to prevent abrasion of  the cables on any sharp edges. 

In every vertical cable ladder, channel, duct, trunking or  cable trench containing cables and exceeding  three meters  in length, internal barriers shall be  provided so  as to prevent the air at the top of the  unit  from attaining  an excessively high temperature.   In  every vertical  cable shaft, cable trench or any  passage  of cable  through  wall, ceiling, floor  barriers  against spread  of  fire  and  smoke  shall  be  provided   for compliance with IEE regulations.  

Where  cable passes through walls, ceiling,  floor,  it shall run through sleeves of PVC pipes or hume pipes of           adequate  diameter.   After pulling the  cable  through sleeves,  both the ends of the sleeves shall be  sealed   water  tight  with fire-resistant material  to  prevent spread of fire and seepage of water.

Generally along each cable route either in trench or in cable  trays/ladders  or in pipe separate Two  Nos.  of earth strips/wires shall run exposed.

Where  an installation comprises medium voltage  cables as well as extra low voltage circuits, precaution shall be  taken in accordance with IEE regulations and  shall  be physically separated by minimum of 300mm distance. 

Metal sheaths and armour of all cables, metal conduits, ducts,  trunking, and bare earth continuity  conductors         associated with such cables, which might otherwise come into  fortuitous  contact with other fixed  metal  work shall  be  effectively bonded there to earth so  as  to prevent   appreciable  potential  difference  at   such  possible points of contact. 

If  it  is necessary to install cables in  a  situation  where   flammable  and/or  explosive  dust,   flammable        volatile  liquid/vapor/gas is likely to be  present  or  where  explosive materials are handled or  stored,  the cabling shall be as per IEE regulations. 

UNDERGROUND INSTALLATIONS

The  cables shall be laid in an excavated trench.   The depth of the trench shall be minimum 750mm., below  the final  ground level but shall be decided on the  number of cables to be laid in the trench so that the vertical distance  between two adjacent layers of  cables  shall not be less than 350mm.  The width of the trench  shall  be  decided on the number of cables to be laid  in  the trench so that the distance between two adjacent cables shall not be less than one able diameter. 

Before laying cables the bottom of the trench shall  be  well compacted and the cables shall be laid on a  100mm fine  sand bedding.  The second layer of 150mm of  fine sand then be spread over the cable and shall be further covered  by  150mm of compacted soil.  For  the  second layer of the cable same procedure shall be repeated. 

The  cables  shall  be  protected  by  placing  precast concrete  tiles or burnt bricks over the cables on  top layer  of sand and for the full length  of  underground cables.   Where more than one cable is running  in  thesame trench, the concrete tiles/bricks shall cover  all  the  cables  and  shall project a minimum  of  80mm  on either side of the cables. 

In  any  case  the top layer of  the  cables  shall  be minimum 600mm below the finished level of the ground. 

The  top  of the cable trench shall be  well  compacted till  the  finished level of the ground  and  shall  be approved  by the Construction Manager.  If  required  a laboratory  compaction  test shall be  carried  out  in  presence of the Construction Manager.

H.V.,  M.V.,  cables  shall not be  laid  in  the  same trench/cable tray and/or along side of water main. 

Cables under road crossings and any surfaces  subjected to  heavy  traffic shall be protected by  running  them through hume pipes of suitable size. 

The  relative position of the cables laid in  the  same trench  shall  be preserved and the  cables  shall  not        cross each other as far as possible.  At all changes in direction in horizontal and vertical planes, the  cable shall  be bent smooth with a radius of bend  not  less than  15  times the diameter of the cable.   Minimum  3  meters  long  loop shall be provided at both  sides  of every  straight joint and 5 meters at each end  of  the cable.  Distinguishing marks shall be made at the cable ends for identification. 

Insulation  tapes  of appropriate voltage and  in  red,  yellow, and blue colors shall be wrapped just below the sockets for phase identification. 

All  the excavation and back fill including  timbering, shoring,  and pumping required for the installation  of  the  cables  shall be carried out as indicated  on  the drawing and as per requirements laid down elsewhere  or as  per  Construction  Manager's  direction.   Trenches shall  be dug true to line and grades.  Back  fill  for trenches shall be filled in layers not exceeding 150mm.  At  each layer compaction test shall be carried out  in  presence of Construction Manager.  Each layer shall  be properly rammed and consolidated before laying the next layer.   The  contractor shall  restore  all  surfaces, roadways,  side  walls, curbs,  walls,  landscaping  or other  works  cut  for  excavation  to  their  original condition,   the  satisfaction  of   the   Construction  Manager.  Suitable approved type cable markers shall be installed  along  the  cable route &  where  change  of direction takes place.

CABLES INSTALLED INSIDE THE BUILDING

The  cables inside the building shall be  installed  in one  of  the  following manner,  as  indicated  in  the drawing and approved by the Construction Manager. 

           INSTALLED IN BUILT-UP TRENCH
The  cables  laid  on  the  bottom  of  the  structural trenches  shall not lie freely upon the trench  bottom. They  shall  be raised to prevent  the  possibility  of  their coming into contact with deleterious materials. 

The  cables laid in the trench shall be laid  on  angle iron     brackets/cable     tray/cable     ladder/cable  troughs/cable  racks as indicated on the drawings,  and as approved by the Construction Manager.  Where  cables  are  clamped to the wall a minimum clearance  of  100mm   shall be maintained between wall and cable and  minimum   150mm  vertical clearance shall be  maintained  between  two  cables.   Where cables are laid  on  brackets  the  brackets  shall not be fixed more than 500mm  apart  to avoid  sag in the cables, where the cables are laid  on cable tray/ladder/troughs/racks, minimum 300mm distance shall be observed between adjacent tier of tray/ladder/ troughs/racks,  and cable shall be fixed  minimum  25mm away  from the wall, and minimum of one cable  diameter distance shall be observed between two adjacent cables. Cables   shall  be  properly  fixed  with   the   tray/ladder/troughs/racks  with  cable  tie  or  saddles  or straps. 

CABLES ON CABLE TRAYS/LADDERS UNDER THE CEILING  OR ON WALL 

Where   cables  are  installed  under/above   suspended ceiling or below ceiling or on wall, they shall be laid on a perforated G.I. cable tray/ladder  type cable tray  and  shall be run in such positions that they  are  not liable  to be damaged by contact with the floor or  the ceiling or other fixtures. 

          The cable tray/ladder shall be properly fixed with  tie rod  to the ceiling.  The concrete inserts  for  fixing the  tie  of shall be put in place while  casting  the slab.   If  insert plates are not placed  in  position,  Anchor fasteners shall be fastened to support cable  trays.  The  cable tray route shall be co-ordinated with  other  services  to  avoid  crisscross of  all  the  services.  

While  laying the cables on the tray minimum one  cable diameter   distance  shall  be  observed  between   two           adjacent cables.  25% space shall be kept spare for any future installation. 

The  trays  shall  be  made  of  16  SWG/12  SWG   G.I. perforated sheet having minimum 50mm depth.  The  width of perforation shall be maximum 10mm spaced at  maximum 20mm  distance.  The width of the cable tray  shall  be selected so as to accommodate required number of cables to  be laid on it, with minimum separation  of  minimum   one  cable diameter between two adjacent  cables.   The cables  shall  be tied with the cable tray  with  nylon strip. 

CABLES INSTALLED IN THE MECHANICAL ROOM
The cable reaching the motors in the mechanical room or plant  room or machines room or service area  shall  be  laid  on cable tray except where indicated  in  masonry underground trenches. 

           The  cable  reaching the motors shall be  protected  by rigid galvanized conduits up to a height of 300mm above   the  floor.   

Above  that  height, the cable shall  be  protected  by means  of oil tight flexible metallic G.I. conduits  to   the terminal box of the motor.  The connection  between the  rigid  conduit and the flexible conduit  shall  be  done by a rewett coupling of an approved type.  

The  flexible conduit shall be properly fixed with  the  terminal box of the motor by means of double  hexagonal   check nut. 

CABLE TRAY/LADDER

          
GI Cable tray shall be manufactured to comply with  the specifications  of National Electrical Code  (NEC)  and  National Electrical Manufacturer's Association (NEMA).  

          
Cable  trays  shall  be  of steel as  per  IS  226  and  galvanised and the thickness of galvanisation shall  be  not less than 110 microns.  All bolts nuts and  washers shall also be galvanised and shall conform to IS  1363-  60   for  quality,  threading  and  dimensions   before galvanising.   Hot dip galvanising shall conform to  IS 2633   Galvanising of each member shall be  carried out  in one complete immersion.  The galvanising  shall  be  uniform,  clear, smooth, continuous and  free  from acid spots.  Quality of zinc used for galvanising shall  be of 98.8% purity.

Cable trays shall generally be of the following type :
 i. for power cables of medium              - ladder type

              voltage and high voltage                    with slotted angles.

            Ii .for control cables and                       - perforated sheet extra 

                low voltage cables                           steel slotted angle type.

           Perforated  cable trays shall be generally  of  channel type and the perforations in the trays shall be  either  8  x 15mm or 10 x 20mm oval  holes.   Control  cables,  extra low voltage cables and instrument cables shall be  laid on perforated cable trays.

Ladder type cable trays shall be made out of 50 x 50  x  6mm slotted M.S. angles for  the rungs and channels  for 

the  side rails.  Pitch of the rungs shall be not  more than 250mm centre to centre.  Rungs shall be welded  to    the side rails.

Cable trays shall be of standard sizes :

          Length          2500mm

          Width           300/450/600/800/1000mm as required.

          Flange of  perforated tray 75/100mm

                    Height of side rail (ladder type) 75mm

          Thickness of sheet steel  - 2.0mm to 3.0mm as per width of tray.

          The  flange  and  width of the  cable  trays  shall  be decided based on the diameter and the number of  cables running through each section of the cable tray. 

         Accessories for Cable Trays

          Following  accessories  of cable  trays,  as  required, shall be supplied with the cable trays.

          Coupler plates

          90 deg bends   - Horizontal and Vertical.

          Tees           - Horizontal and Vertical.

          Reducers

          4-way cross

          Tray covers

          Fasteners.
     Accessories also shall be hot dip galvanised, thickness of galvanising being not less than 110 microns. 

         TESTING         

          Prior  to  laying cables, and prior to  energizing  the cables, following tests shall be carried out :-

          Insulation Resistance test between phases and phase  to neutral and phase to earth. 

          Continuity  test of all the phases, neutral  and  earth continuity conductor. 

          Sheathing continuity test.

          Earth resistance test of all the phases and neutral.

All  tests  shall  be carried out  in  accordance  with  relevant  Indian Standard Code of practice  and  Indian  Electricity   Rules.   The  Contractor  shall   provide  necessary   instruments,  equipments  and  labour   for conducting  the above test and shall bear all  expenses in  connection  with such tests.  All  tests  shall  be  carried out in the presence of the Construction Manager    and results shall be recorded in the prescribed forms. 

STORING :

All the cables shall be supplied in drums.   On receipt of  cables at site,  the cables shall be inspected  and stored  in  drums  with flanges of the  cable  drum  in vertical position. The end of the cable shall be sealed for water tightness.

           MEASUREMENT
Mode of measurement is as follows :

All  power  cables  including  fixing  accessories  as described  in  specifications and SOQ are  measured  in  linear metre (Rm). Power  cable terminations are measured  in  Number (No)
 Control cables including terminations are  measured in linear metres (Rm)

 Cable  trays and conduit/pipes are measured  in  linear  metres (Rm). 
D.         LIGHT FITTINGS AND ACCESSORIES :

             SCOPE
Scope   of  work  under  this  section  shall   include inspection  at suppliers/manufacturer's premises,    appropriate,   receiving   at   site,   safe   storage,   transportation  from  point  of  storage  to  point  of  erection  and erection of light fittings, fixtures  and  accessories including all necessary supports, brackets,  down  rods  and painting as required.   The  contractor shall supply all materials and accessories (other than  those   supplied   by  the   owner),   labour,   tools,  transportation,  scaffolding  etc.,  required  for  the completion of above work in all respects.

             STANDARDS APPLICABLE :

The  lighting and their associated accessories such  as  lamps,  reflectors,  housings,  ballasts  etc.,  shall comply  with  the  latest  applicable  standards,  more specifically the following :

            Electric   light  fittings General and safety  requirements  -   IS - 1913.

             Industrial lighting fittings with  metal reflectors                -   IS - 1777

             Decorative lighting outposts                                                  -   IS - 5077

             Flood Lights                                                                            -   IS - 1947

             Luminaries for street lighting                                               -   IS - 2149

             Bayonet lamp holders                                                            -   IS - 1258

             Bi-pin lamp holders for tubular fluorescent lamps              -   IS - 3323

             Ballasts for use in fluorescent light fittings                         -   IS - 1534

             Starters for fluorescent lamp                                                -   IS - 2215

             Ballast for HP MV lamps                                                      -   IS - 6616

             Capacitors for use in fluorescent,  HPMV  &  LP  sodium  

             Vapour  lamps  circuits                                                         -   IS - 2215

             Tubular Fluorescent lamps                                      -   IS - 2418 (Part I)

             High pressure mercury vapour lamps                                   -   IS - 2183

             Tungsten filament general electric lamps                             -   IS -  418

              High pressure sodium vapour lamps                     -   IS - 9974 (Part -I)

              Light Fittings - General Requirements :

       a)     Fittings  shall be designed for  continuous  trouble  free operation under atmospheric conditions,   reduction  in lamp life or without deterioration  of   materials  and  internal wiring.  Outdoor  fittings  shall be weather - proof and rain proof.

       b)   Fittings shall be so designed as to facilitate  easy maintenance   including  cleaning,  replacement   of  lamps/starters etc.

       c)     All fittings shall be supplied complete with  lamps.  All  mercury vapour and sodium vapour lamp   fittings shall  be complete with accessories  like  ballasts,  power factor improvement capacitors, starters, etc.  Out  door  type  fittings  shall  be  provided  with  weather proof boxes.

       d)    Fluorescent lamp fittings shall be complete with  all  accessories  like ballasts, power factor  improvement capacitors,  starters  capacitors for  correction  of  stroboscopic effect.

       e)     Each  fitting shall have a terminal  block  suitable  for  loop-out  connection by 1100  V  PVC insulated copper  conductor wires upto 4 sq.mm.  the  internal wiring  should be completed by the  manufacturer  by  means of standard copper wire and terminated on  the terminal block.

       f)      All  hardware used in the fitting shall be  suitably plated  or  anodised  and  passivated  for  use   in industrial plants.

       g)     Earthing  Each light fitting shall be provided  with an  earthing terminal.  All metal or metal  enclosed parts  of the housing shall be bonded and  connected to  the earth terminal so as to ensure satisfactory  earthing continuity throughout the fixture.

       h)     Painting/Finish  All surfaces of the fittings  shall be thoroughly cleaned and degreased and the fittings shall  be  free from scale, rust,  sharp-edges,  and  burrs.

i)  The housing shall be stove-enamelled or anodised  as required.   The surface shall be  scratch  resistant and shall show  no sign of cracking or flaking  when bent through 90 deg. over 12 mm dia mandrel.

              DECORATIVE TYPE FITTINGS
                Decorative fluorescent fittings shall be provided  with mounting/housing  channel cum reflectors of CRCA  sheet steel.  Stove enamelled diffusers or louvers  shall  be  translucent white polystyrene.

              ACCESSORIES FOR LIGHT FITTINGS REFLECTORS :
                The   reflectors   shall   be  made   of   CRCA   sheet steel/aluminium/silvered  glass/Chromium     plated  sheet copper as required.  The thickness of reflectors  shall  be as per relevant standards. Reflectors made of steel shall  have  stove  enamelled/vitreous  enamelled/epoxy  coating finish.  Aluminium used for reflectors shall be anodised/epoxy  stove  enamelled/mirror  polished.  The finish  for the reflector shall be as  specified.   The reflectors  shall be free from scratches  blisters  and  shall  have  a  smooth and  glossy  surface  having  no premium light reflecting coefficient.  Reflectors shall be readily removable from the housing for cleaning  and maintenance without use of tools.

              LAMP/STARTERS HOLDERS :
                Lamp  holders  shall have  low  contact  resistance, shall  be resistant to wear.  They shall hold lamps  in position under normal conditions of shock and vibration   prevalent in an industrial atmosphere. Lamp  holders for fluorescent lamps shall be of  spring loaded  BI-pin  rotar  type.  Live parts  of  the lamp holder shall not be exposed during insertion or removal of the lamp or after the lamp has been taken out.

                Lamp holders for incandescent and mercury vapour  lamps shall be bayonet type upto 100 W and Edison screw  type  for higher wattage. Starter  holders  for  fluorescent lamps  shall  be so designed that they are mechanically robust and shall be capable   of   withstanding  shocks during   transit,  installation and use.

               BALLASTS :

                The  ballasts shall be designed for long life  and  low power  loss. They shall be mounted using   self-locking, anti  -vibration fixtures and shall be easy  to  remove without demounting the fittings.  The enclosures  shall be dust tight and non-combustible. Ballasts  shall be inductive, heavy duty  type,  filled with  thermosetting,  insulating,  moisture   repellent polyester compound  filled  under pressure or  vacuum.   Ballasts shall  be provided with taps to set the  voltage.   The ballast  wiring  shall be of copper and they  shall  be  free from dust.

                Separate ballast shall be provided in case of multilamp fittings, except in case of 2 x 20 W fittings. Starters   shall  have  bi-metal  electrodes  of   high mechanical  strength.   Starters shall be replaceable without  disturbing the reflector of lamps and  without  use of any tool. Starters shall have brass contacts and radio interference suppression capacitor.

             CAPACITORS :

                The   Capacitors  shall  have  a  constant   value   of capacitance and shall be connected across the   supply of individual lamp circuits. The  capacitor shall have a value of capacitance so  as to  correct the power factor of its corresponding  lamp circuit  to  0.95  lag or better.  Capacitor  shall  be  hermetically sealed preferably in a metal enclosure  to prevent seepage of impregnant and ingress of moisture.

              LAMPS :

                Incandescent lamps shall be clear type unless otherwise  specified.   Fluorescent  lamps  shall  be   "day-light colour"  type unless otherwise specified and  shall  be provided  with  features to avoid blackckening  of  lamp ends. Mercury vapour lamps shall be of high pressure,  colour   corrected type. Lamps  shall  be  capable  of  withstanding  vibrations  prevalent in an   industrial    atmosphere,    the  filament/electrodes   shall   not  break   under   such circumstances.

                PL Lamps shall be energy effective compact single ended light  sources  in 9 to 11W ratings consisting  of  two narrow glass tubes welded together. The  lamp shall be complete with integral  glow  switch starter   and   capacitor  and   two   pin   electrical  connection The  lamp shall be colour rendered to give warm  colour impression. The  compact lamp shall have a long life and  shall  be energy efficient.

  
 INSTALLATION :

               The light fixtures and fittings shall be assembled and installed in position complete and ready for service, in accordance with details, drawings, manufacturer’s instructions   and   to   the satisfaction   of   the Construction Manager.  Pendent fixtures specified  with overall stem lengths are subject to change and shall be checked  with  conditions on the job and  installed  as   directed.   All  suspended fixtures  shall  be  mounted rigid   and  fixed  in  position  in  accordance   with drawings,   instructions  and  the  approval   of   the  Construction Manager.  Fixtures shall be suspended true to alignment, plumb, level and capable of resisting all lateral  and  vertical  forces and shall  be  fixed  as required. 

All suspended light fixtures, fans etc, shall be provided with concealed suspension arrangement in the concrete  slab/roof  members.  It is the  duty  of  the Contractor to make these provisions at the  appropriate stage of construction. Exhaust fans shall be fixed  at location  shown on drawings. They shall be wired to  a plug  socket outlet at a convenient location near the fan. All switch and outlet boxes, for fans and  light fittings  shall be bonded to earth.  The recessed  type fixtures shall not be supported into the false  ceiling  frame  work. This shall have independent support from the socket of ceiling using G.I.conduit down  rods/chromium

plated  steel chain with  provision  for adjusting  the  level  of  fitting.   Wires  shall   be connected  to  all fixtures through  connector  blocks. Wires brought out from junction boxes shall be  encased in flexible pipes for connecting to fixtures  concealed in  suspended  ceiling.  The flexible  pipes  shall  be check-nuted  to the junction box with a brass bush  and double  checknut  at the fixture  and  flexible  pipes,  wherever used shall be of make and quality approved  by the Construction Manager/Architect. 

               MEASUREMENT

              MODE OF MEASUREMENT IS AS FOLLOWS :

                Installation  of  light fittings  with  all  associated  works  including  fixing  accessories  is measured  in  numbers (No) Supply  and  installation of down rods and  C.P.  chain with associated works as per SOQ and specifications are measured in linear metre (Rm).

E.   ADVANCE LIGHTNING PROTECTION SYSTEM:
Scope

Involves supply, installation, testing and commissioning of Advanced Lightning Protection consisting of Air Termination. Air Termination support, down conductors, earthing, performance recording equipment etc., as required complete.

1.
The Advanced lightning protection system shall include:-


(a) air termination(s) 


(b) mechanical support(s) 


(c) low impedance insulated down conductor(s) 


(d)  performance recording equipment, and 


(e) a low impedance grounding system.

2.
The Advanced lightning protection system shall have :-

a.
an air terminal of the type designed to minimise corona emissions and optimise streamer inception when optimum pre-determined conditions are met. 

b.
shall be mounted adequately rated for wind loading. Guy sets shall be provided as appropriate to local environmental conditions.

c.
shall be designed by a reputed company in the manufacture and development of Advanced Lightning  system components, of types, sizes and ratings and, who can produce support that their products have been in service for a long time and performance is in satisfactory condition. 

d.
shall be installed strictly to the manufacturer’s instructions. 

Air Terminal

1.
Shall respond dynamically to the appearance of a lightning down-leader, shall be designed to trigger in relation to the optimum pre-determined conditions for upward leader inception. The triggering conditions must dynamically adjust to reflect the down leader intensity, building height above ground and the other factors that effect the electric field intensification above the air terminal. 

2.
Shall incorporate a curved conductive surface spaced from a permanently grounded central finial. During triggering of the air terminal the curved conductive surface shall be temporarily grounded, thereby producing an increase in electric field directly above the air terminal.

3.
The air termination shall be designed :-

a.
With a range of optimal finial tip radii to match the different electric field conditions the terminal is subjected to at various installation heights above the ground level.

b.
Arcing at the finial tip is not to be continuous and shall only occur during the process of lightning leader approach. Arcing shall not occur solely due to electro-static field created by the presence of charged overhead thunderclouds.

4.
The materials used for the terminal shall be non-corroding in any type of environments. The centre grounded electrode tip shall not be less than 20mm diameter, the curved conductive surface shall be of a conductive material of thickness as defined in IEC61024.

5.
The collection volume and attractive radius of the air termination shall be traceable to known and acceptable lightning research and statistics.

6.
The isolating material supporting the curved conductive surface from the centre grounded electrode shall be of glass/mineral reinforced polypropylene. This material used shall have the following properties, high impact strength, UV stabilized, high electrical dielectric, high comparative tracking index and operating heat capability up to 120°C continuous.

7.
The protective zone provided shall be such that it becomes the preferred strike point for all discharges exceeding a peak amplitude return strike current as per IEC61024. The design shall take account of upward leader competing projections on the structure. 

	Strike Current
	Levels of Protection 
	Exceedance Probability

	2.9 kA
	Protection Level I – Very High
	99%

	5.4 kA
	Protection Level II- High
	97%

	10.1 kA
	Protection Level III – Medium
	91%

	15.7 kA
	Protection Level IV – Standard
	84%


Air Termination Support

1
The air terminal support shall consist of a minimum of 2m of insulating re-enforced fibreglass cylindrical mast. The conductor shall pass through the centre of the mast, with the high voltage termination contained to the upper 1m of the mast.

2.
The support shall be securely bolted to other mast materials with guy wires used where necessary to enable the air termination and mast system to withstand maximum locally recorded wind velocities and pressure.

Downconductor 

The downconductor shall 

a.
Consist of a plastic filler, copper conductor, inner insulation, outer copper conductor, conductive sheath, all concentrically arranged and defined by the manufacturer.

b.
Have a low characteristic impedance of 4.5 ( (Ohms) and a maximum inductance of 22 nH/m.

c.
Have the capacitance equal to 1100 or greater than 1000 pF/m and the resistance should be equal or less than 0.5 (m(/m).

d.
To be tested in a lab to withstand a lightning impulse rating of (250KV peak voltage between the core & screen based 1.2/50µs-wave shape as defined under ANSI C62.41.

e.
The outer diameter of the downconductor shall be less than 35mm.

f.
The main copper conductor shall be made of electrolytic grade copper of minimum cross sectional area of 50mm².

g.
At the end, 3m to the ground and where it is exposed to human intervention, the downconductor shall be placed in a protective rigid PVC pipe of 3mm minimum wall thickness to avoid mechanical damage.

h.
The main copper conductor shall be capable of direct connection to the base of the air termination by use of a compression coupling.

i.
The downconductor shall be installed as per the manufacturer's instructions and should not be subject to bends of less than 0.5 metres radius.

j.
The downconductor after routing, must be connected in the conductive clamps. The top 10% of the installed length must be anchored at least every 1 metre and the lower be anchored at least every 2 metres.

k.
The downconductor(s) shall be in conformity with UL-96: Lightning Protection Components (Standard for safety)

Performance recording equipment

1.
Each protection system shall be supplied with a lightning event counter. The lightning event counter shall have an register that activates one count for every discharge where the peak current exceeds 1500A. The test wave shape shall be the 8/20us standard as defined by ANSI C62.41

2.
The lightning event counter shall be of robust, easy to install and housed in a IP67 rated enclosure. The counter shall operate from the energy of the lightning discharge and not depend on external or battery power to operate.

3.
The lightning event counter shall be installed to the manufacturer’s instructions in a readily accessible manner so that readings can be taken at regular intervals. It shall be positioned such that its operating temperature is within the range -10(C to +50(C.

Grounding

1.
The grounding system reading shall not exceed 10 ohms static impedance except with prior approval by the EB or manufacturer of the Advanced Lightning  protection system. 

2.
Grounding shall be affected by copper wire or tape buried below the frost line (or to approximately 600mm deep in non freezing locations) or by deep driven UL listed copper bonded steel core ground rods with at least 10mil copper thickness. 

3.
Bonding of the grounding system to all metallic parts of the building, including structural reinforcing steel is preferred. The resistance should be measured and the 10-ohm requirements achieved before such bonding is affected.

4.
Electrically conductive Ground Enhancing Materials may be used to achieve low ground resistance provided the materials are mixed and strictly in accordance with the manufacturer’s instructions
METHOD OF MEASUREMENT
       The earth conductor (G.I. or Aluminium strip) including all accessories is measured in linear metre (Rm).

       The  air termination including support is  measured  in Number (No)

       Earthing   stations  with  all  associated  works  as described in SOQ are measured in number (No).
F.        EARTHING SYSTEM
SCOPE

This  section  covers the  requirements  for  providing  "Earthing" connection to metal parts of equipment etc., The  contractor  shall supply  all  materials,  labour, tools,  plant  etc., and everything necessary  for  the complete Earthing installation".

STANDARDS APPLICABLE

The following standards shall be applicable :

IS 3043  -Code of practice for earthing.

IEEE - 80:86.

IEEE - 142:92.

GENERAL

All the non-current carrying metal parts  of electrical installation  shall  be earthed as per IS:  3043.   All equipment, metal conduits, rising main  cable  armour,  switch  gear,  distribution boards, meters,  all  other  metal  parts forming part of the work shall  be  bonded  together  and  connected by two separate  and  distinct  conductors  to earth electrodes. Earthing shall  be  in conformity with the provisions of Rules 32, 61, 62,  67 and 68 of IER 1956.

G.I.PIPE EARTH STATION  : 

Electrodes  shall  be  made of G.I.  pipe  of  internal diameter of 40mm dia.  The pipe electrode shall be  as  far  as practicable embedded below  permanent  moisture  level.   The length of the pipe electrode shall not  be   less  than  2.5 m.  Except where rock  is  encountered, pipes  shall  be driven to a depth of at  least  2.5mtr where  rock  is  encountered at a depth  of  less  than  2.5mtr. The  electrode may be buried  inclined  to  the vertical  and the inclinations not more than 30  deg  C  from the vertical.  The pipe electrode shall be made of one piece.  Earth leads to the electrode shall be  laid  in  a  heavy  duty GI pipe and connected  to  the  pipe  electrode with brass bolts, nuts and washers.  GI  pipe  shall  be  terminated  in a wire  meshed  funnel.   The  funnel shall be enclosed in a masonry chamber of  450mm x 450mm dimensions.  The chamber shall be provided  with C.I. frame and CI inspection cover.  The earth  station  shall  also  be  provided  with  a  suitable  permanent identifications  label tag.  The earth electrode  shall  conform to IS:3043 latest edition.  The soil around the  earthing  electrode  shall  be treated  to  reduce  the   resistivity  of the soil by filling the complete  depth of  electrode with alternative layers of  charcoal  and  salt. 

PLATE EARTH STATION 

Plate electrodes shall be made of copper (CU) plate  of   3mm  thick  and 600 x 600mm size.  The plate  shall  be   buried   vertically  in ground at a depth of  not  less  than  2.5  meters to the top of the  plate,  the  plate  being          encased in charcoal to a thickness of 300mm  all    round.   It is preferable to bury the electrode to a depth  where subsoil water is present.  Earth leads  to  the electrode shall be laid in a heavy duty GI pipe and connected to the  plate electrode with brass bolts, nuts  and washers.  A GI pipe of not less than 19mm dia shall   be  clamped  with bolts vertically to  the  plate  and   terminated  in a wire meshed funnel.  The funnel  shall be  enclosed  in  a   masonry chamber of  450mm  x  450mm  dimensions.   The  chamber shall be  provided  with  GI   frame and CI inspection cover.  The earth station shall  also  be provided with a suitable  permanent  identifications  label tag.  The earth electrode shall  conform to IS:3043.

EARTHING CONDUCTORS 

All  earthing conductors shall be of high  conductivity copper and shall be protected against mechanical damage  and  corrosion.   The connection  of  earth  electrodes shall  be strong secure and sound and shall  be  easily      accessible.   The  earth conductors  shall  be  rigidly fixed  to  the  walls, cable  trenches,  cable  tunnel, conduits and cables by using suitable clamps.

Main  earth  bus shall be taken from  the  main  medium voltage  panel to the earth electrodes. The number of        electrodes  required  shall be arrived at  taking  into  consideration  the  anticipated  fault  on  the  medium  voltage net work.

Earthing conductors for equipment shall be run from the exposed metal surface of the equipment and connected to a suitable point on the sub main or main earthing  bus.  All  switch boards, distribution boards  and  isolators disconnect  switches  shall be connected to  the earth,  bus.   Earthing conductors shall be terminated  at  the equipment using suitable lugs, bolts, washers and nuts.

All  conduits cable armouring etc.,  shall be connected to the earth all along their run by earthing conductors   of  suitable  cross  sectional  area.   The  electrical resistance  of earthing conductors shall be low  enough  to  permit  the passage of fault current  necessary  to operate  a fuse/protective device or a circuit  breaker and shall not exceed 2 ohms.

PRECAUTIONS                   
Earthing  system shall be mechanically robust  and  the joints  shall  be capable of retaining  low  resistance   even after subjection to fault currents.
Joints   shall  be  tinned,   soldered  and/or   double rivetted.   All  the  joints shall be mechanically  and  electrically continuous and effective.  Joints shall be protected against corrosion.
TESTING          
On  the  completion of  the  entire  installation,  the following tests shall be conducted :
          i)   Earth resistance of electrodes
          ii)  Impedance  of earth continuity conductors  as  per is 3043.  
         iii)  Effectiveness of earthing as per is 3043. 
All meters, instruments  and labour required for  the tests  shall be provided by the contractor.   The  test  results shall be submitted in the prescribed  tabulated form in triplicate to the consultants for approval.
MEASUREMENT
Mode of measurement is as follows :

Earth strips (GI/Cu), earth conductor are measured in linear metre (Rm).

Earthing station with all associated works (G.I pipe or copper plate) is measured in number (No).

G.
DATA AND VOICE NETWORKING SYSTEM

1.0
INTRODUCTION:

1.1
This tender shall act as a guide to the type of system desired for the project. The specifications described in this tender are as per the Basis of Design and are the minimum required from the contractor. 

1.2
Standard literature not complying to the format and the requirements of this tender, shall not be considered or evaluated. 

2.0        Installation :

2.1
Contractor shall take written approval from the Project manager for the storage of any equipment at site. The location of any stored equipment   shall be coordinated with the Project manager. 

2.2         Damage caused by the contractor during installation and testing must be replaced or repaired by the contractor at no cost and to the satisfaction of the project manager.

2.3 After the contract is awarded, but before the contractor orders the cables and equipment components, the contractor shall submit to the project manager, samples and part numbers of the cables for approval before they are ordered. For composite cables, sample of each section of the composite cable is adequate.

2.4 The contractor shall obtain all manufacturer’s instructions including current bulletins, for the installation of the cables and cabling system components provided by the contractor. Copies of these documents and all manufacturer warranty documents shall be submitted by the contractor to the project manager when the installation of the cable begins.

2.5
The contractor shall provide the necessary protection and care, to safe guard his own work as well as the work of other agencies. Care shall be taken not to damage false ceiling tiles and conduits provided for electrical wiring.

2.6 The contractor shall provide all necessary tools, hardware and test equipment needed by their labourers to install, label, test and document the total cabling system.

2.7 The installation of the data and voice systems by the contractor shall not be considered complete until all cables and components described in this specification are installed, labelled, tested and the documentation is delivered according to the specifications, and also the successful inspection from the project manager.

2.8 The contractor is fully responsible for the co-ordination of the works at the site with respect to other services.

2.9 The contractor is responsible for hoisting and transporting the materials into the building.

3.0 SCOPE OF WORK

3.1 Supply, install, test and label Data category 5/5E/6, twisted pair, 24AWG wire in locations specified on the enclosed drawings, specifications and schedule of works. This is for a local area network from each location marked on the floor plan and attachment to the patch panel on the free standing cable rack in the appropriate wiring closet.

3.2 Wiring closets and hubs are located in the room as marked on the floor plan.

3.3 All work shall be according to Category 5/5E/6 specifications as published in EIA/TIA 568-A. Additions are listed in TSB 31, 36 and 40. In addition, all installation shall be in compliance with ISDN BRI (ISO 8877). Cable connectors shall meet the IEEE 802.3 (100BASE TX) and IEEE 802.31 (10 BASE T) specifications. Where there is a gray area, the following guidelines will be the principal deciding factors.

4.0 CONDUIT AND CABLE BENDS AS CURRENTLY INSTALLED

4.1 In the case that wall / floor mounted race way is used, there shall be at least 30% of empty space. All conduit diameters must comply with the limitations of number of cables as per the following table :

	Conduit diameter trade size
	Wire OD of the cables

               0.19
	0.24
	0.31
	0.37



	0.50
	1
	0
	0
	0

	0.75
	5
	3
	2
	1

	1.00
	8
	6
	3
	2

	1.25
	14
	10
	4
	3

	1.50
	18
	15
	6
	4

	2.00
	26
	20
	12
	7

	2.50
	40
	30
	13
	12

	3.00
	60
	40
	20
	17

	3.50
	
	
	
	22

	4.00
	
	
	
	30


4.2
The bending radii shall be as follows :

	Scenario
	Bend Radius



	<  50mm
	6 x internal diameter of the conduit



	> 50mm
	10 x internal diameter of the conduit



	Fiber pull
	10 x internal diameter of the conduit




4.3
No section of conduit shall be longer than 35m or contain more than two 90( bends between pull boxes.

4.4 Any single conduit run starting from the wiring closet shall not serve for more than three outlets.

4.5 Neatness in cabling, ensuring that all cables are hidden from the open view or run in the raceway, is mandatory. Cables shall not be stapled to walls, abutments, supports, or any other objects. Concurrent data cable runs shall be bundled neatly and loosely.

4.6 Cable entrance paths or conduit runs shall be recorded electronically and that information shall be provided to the client in a tab-delimited spread sheet.

4.7 Where wall mounted raceway is run horizontally, it shall be fastened mechanically as per the manufacturer’s specification and the connection joints shall be centered between the vertical standard brackets.

4.8 All wall mounted race way shall run parallel to the floor and shall be mounted at the minimum acceptable distance from the floor.

5.0 TELECOMMUNICATION OUTLETS AND CONNECTORS
5.1
Drop cable specifications: 

5.1.1
All drop and patch cables shall not exceed 1.5m.

5.1.2 The total length of the drop and patch cables shall be not more than 7.5m. All patch and drop cables shall be category 5/5E/6 rated, as explained in section 6.

5.1.3 While testing for certification, drop and patch cables shall be used in place of the cables supplied with the testing equipment.

5.2 Connector specifications :

5.2.1 Each 4 pair 24AWG category 5/5E/6 cable shall be terminated in an 8 pin modular jack at the work area. These connectors shall be 100 ohm, UTP outlets that meet all criteria listed in EIA/TIA 568 sections 12.2.5 and 12.2.6.

5.2.2 The pin / pair assignments shall be according to the 568A designation with applicable colour code combinations. The pin/pair assignments are compatible with ISDN / BRI (ISO 8877) reference B1.24.

5.2.3 Each drop shall have a MOD-TAP flush mounted or box jack face plates installed for data. In most instances jacks shall contain RJ45 jacks or blanks. Where appropriate, thre MOD-TAP face plates may be fitted for phone jacks (RJ11) for phone use as well as RJ-45 jacks as long as all open for fitted for blanks.

5.2.4 Only jacks, faceplates, gang boxes and blanks inventoried to be in the client’s possession. After inspection shall be charged to the client.

6.0 WIRING DESCRIPTION FOR CAT 5/5E/6 HORIZONTAL CABLING

6.1
All cables with a run length of 90m or less shall consist of 24AWG thermoplastic insulated conductors formed into four twisted pair and enclosed by a thermoplastic jacket.

6.2 If the cable is to be plenum-rated it must be covered with teflon fire retardant for plenum (CPM) rating. All cables shall be rated by the manufacturer to be certified Category 5/5E/6 compliance.

(Note : The contractor shall submit a notice, if any of the single lengths is exceeding 90m)

6.3 The wire OD of the UTP copper cable shall be not more than 0.21.

6.4 The pair assembly shall meet the colour code according to EIA/TIA 568A.

6.5 Wires shall not be bent tightly or kinked at the jack or elsewhere or bent less than 6.5OD of the cable.

6.6 Cable shall be tested by the third party once installed and shall perform better than the minimum requirements outlined in EIA/TIA 568A- section 10.

6.7 If any cable fails to meet the specified requirements, during testing measurements by the third party or conflict with the contractor’s test results, the cable shall be completely reinstalled at the contractor’s expense including equipment, parts and time.

6.8 The length of the cables shall be recorded using cable test equipment. Only cable (+ a standard deviation) that has been recorded will be paid for by the Client.

6.9 All the excess cable shall be returned to the contractor at no charge to the client.

7.0 ELECTRICAL CONSIDERATIONS:

7.1
All wires shall be run as per the following table:

	Condition
	< 2 kVA
	2 – 5 kVA
	> 5 kVA

	
	
	
	

	Unshielded power lines or electrical equipment in proximity to open or non metal pathways


	5”
	12”
	24”

	Unshielded power lines or electrical equipment in proximity to a grounded metal conduit pathway


	2.5”
	6”
	12”

	Power lines enclosed in a grounded metal conduit (or equivalent shielding) in proximity to a grounded metal conduit pathway
	
	3”
	6”


7.2 All wires shall be run at least 2m from electromagnetic fields such as those generated by electrical motors, convertors and invertors.

7.3 All wires shall be run at least 6” from fluorescent lights.

7.4 All concurrent wiring runs paired with electronic cabling shall not exceed 3’ in length.

8.0 WIRING CLOSETS :

8.1
The wiring closets are a transition point between the horizontal distribution pathways and all or part of the back bone.

8.2 The wiring closets shall contain one or more floor/wall/ceiling mounted racks. Each rack shall be no taller than eight feet and exactly 19” wide. Each rack shall have at least four shelving units.

8.3 Multiple closets on a floor shall be interconnected by a minimum of one conduit trade size three or equivalent.

8.4 The wiring closets shall have a 24hour, thermostat controlled, HVAC system or shall operate in a range of 64-75deg F with 30-50% relative humidity.

8.5 Drainage troughs shall be placed under the sprinkler pipes to prevent leakage on to the equipment within the room.
9.0 MAIN CLOSET :

9.1
The main closet is the centralised space for telecommunication equipment.

9.2 This room shall house only the equipment directly related to telecommunications system and its environmental support system.

9.3 Each rack shall be no taller than eight feet and exactly 19” wide. Each rack shall have at least four shelving units. Additional shelving may be built at this time for all servers. 

9.4 The wiring closets shall have a 24hour, thermostat controlled, HVAC system or shall operate in a range of 64-75deg F with 30-50% relative humidity.

9.5 Drainage troughs shall be placed under the sprinkler pipes to prevent leakage on to the equipment within the room.

10.0 DISTRIBUTION RACK SPECIFICATIONS:

10.1
Equipment Racks:

10.1.1
Each rack shall be allocated with no more than 200 wiring terminations.

10.1.2 Racks shall have clearances of at least 30” to the rear, 36” in front and 14” on the sides for access and cable dressing space.

10.2 Grounding and Bonding :

10.2.1 Cross connect hardware for cabling shall be mounted on frames that will accommodate a grounding conductor that will provide a path of low DC resistance to ground. The grounding conductor shall be bonded to the same grounding system that is employed by the power service as the cross connect equipment.

10.2.2 The grounding conductor shall not be less than 6 AWG.

10.3 Patch Panels (Connecting Hardware)

10.3.1 The transmission properties of internally wired connecting devices shall meet  the transmission performance requirements specified in EIA/TIA 568A section 12.2.6.2 interfaces included.

10.3.2 Standard telecommunication interface jacks and plugs shall meet the requirements of EIA/TIA-TSP-31, ref B1.37.

10.3.3 Telecommunication interfaced jacks shall be 8 pin jacks with pin/pair assignments according to 568A designation applicable with colour code combination. These pin/pair assignments are compatible with ISDN BRI (ISO 8877).

10.4 JUMPER CABLES:

10.4.1 Cross connect jumpers and patch chords shall meet the minimum performance requirements specified in EIA/TIA 568A.

10.4.2 The use flat non twisted chords is strictly prohibited.

10.4.3 The cables shall consist of a male connectors at both the ends, RJ45 connectors as specified in IEEE 802.3(10BASE2).

10.4.4 
 Each jumper cable shall not exceed 3m in length.

11.0 WIRING LABLES AND WIRE MANAGEMENT

11.1
Labelling all wall jacks, cables patch cables, patch panel, patch panel jacks is mandatory. The method for applying labels shall be left to the discretion of the contractor.

11.2 Labels themselves shall be according to the Jack ID description.

11.3 The cable conduit entrance path shall be marked on the floor plans and following completion of the work, a blue print shall be provided to the client depicting all locations and label Ids of each jack and patch panel.

12.0 TESTING AND SITE CERTIFICATION

12.1 The contractor shall perform all cable testing once and then the second time by a qualified technician.

12.2 All copper cables shall be tested by a certified calibrated phase 2 micro test Penta scanner according to an accepted and approved category 5/5E/6 test procedure.

12.3 All test shall be saved in memory within the tester until a Project manager can down load them to a tab delimited test file.

12.4 No test measurements shall be accepted that are not down loaded directly from the Penta scanner. Test performed by the contractor shall be verified for necessary accomplishments by the consultants.

12.5 Any test in question shall be run a third time in the presence of Project manager, the contractor and the third party testing authority. This shall be considered a final test and the contractor shall record the results accordingly.

12.6 Any cable runs that fail to meet specifications and fail the Penta scanner test shall be completely re-installed at the expense of the contractor.

12.7 Further testing expenses shall be paid by the client to the testing authority.

12.8
The contractor shall get the site certified from the OEMs for a period of at `least ten years and submit the documents on the day of hand over of the project.

12.9
The contractor is responsible for any defects in the functioning of the system during defects liability period. The contractor shall submit the complete details of manufacturer’s address and contact numbers to the client for any future requirements.  

13.0 DOCUMENTATION

13.1 
All cables implementation shall be documented.

13.2 Site built drawings in A3 size shall be submitted to the client.

14.0 GENERAL CONSIDERATIONS:
14.1
Rules, codes and regulations

14.1.1

All work and materials shall be in full accordance with the latest rules, codes and regulations.

14.1.1 Nothing on the drawings or in the specifications shall be construed to allow work not in conformance with these rules and regulations.

14.1.2 The drawings and specifications shall take precedence where work and material described there in exceeds that required by rules, codes or regulations.

14.2 Permits, fees and inspections

14.2.1 The contractor shall obtain all permits and license required and pay all fees incidental to the installation.

14.2.2 The contractor shall provide the client with the schedule of inspections where applicable and submit all certification of inspection.

14.3 Guarantee:
All  work,  material and equipment shall be  guaranteed to be free from defects in workmanship or material for a period of one year from the date of issue of completion certificate from the project manager. The contractor shall repair or replace all such defects in a timely manner and damage to the client’s property resulting from such defects and repairs thereof. All equipment and material provided and all work accomplished under the requirements of this section shall be at no expense to the client.

14.4 As built drawings:
14.4.1 The contractor shall keep a separate set of drawings at the job site to be used as AS BUILT drawings. These drawings are to be kept current and in a neat and clean conditions all the time.They are to be available for inspection by Project managers at any time during site visits. These drawings shall be red lined to indicate all changes in equipment, devices and outlet locations and to indicate the true locations of all concealed or underground work where different from that shown on the drawings. Each sheet of this set shall be cleared and permanently marked “AS BUILT”.  

14.4.2 Upon completion of the project and prior to the final payment, the contractor shall purchase a fresh set of prints from client and transfer all AS BUILT information to it. All information shall be clearly drawn with ink. The contractor shall deliver two sets of final AS BUILT drawings to the architects and the client for approval.

15.0 Products :

15.1
Materials:

15.1.1
Unless specifically indicated otherwise all materials shall be new and free from defects. It shall be listed by Underwriter’s laboratories where applicable.

15.2.1 Submittals:
15.3 Material submittals shall be complete and submitted all at the same time. The individual group of submittal types such as wires, face plates, patch panels etc shall be prefaced with a list of contents identifying each item by its project name, manufacturer and complete catalog number. Each copy of the submittal group shall have the list of contents attached.  The contractor is responsible for submitting this information in a timely manner so that material may be ordered early enough to meet the construction schedule. If the material is not ordered in time for whatever reason, pay such premium prices, special handling charges as required to meet the construction schedule. No substitution of an accepted item will be allowed due to the failure to plan for adequate material procurement lead time.
15.4 Cutting and patching :

The contractor shall obtain project manager’s approval prior to cutting existing surfaces or surfaces under construction. All such surfaces shall be repaired or patched to the satisfaction of the architect.

15.5 Protection, Cleaning and Repairs :

15.5.1 Protect all equipment from damage and degradation during construction. Equipment stored shall be protected from dust, water and damages from the other sources.

15.5.2 After completion of work, prior to final review from the client, the equipment shall be thoroughly cleaned of all dirt, water, grease, plaster, paint or any construction debris. All surfaces shall be clean and in new condition. All such defacements as scratches, dents, marks and checks shall be repaired to the satisfaction of the project manager or the equipment shall be replaced at no additional cost
COVID-19 SAFETY INSTRUCTIONS TO CONTRACTORS
1. PURPOSE:
To safeguard the workers from Corona virus (Covid-19), Contractor shall be strictly adhering the guidelines received from Govt. at all project sites and plants.
2. SCOPE:

These guidelines applicable to all Contractors only.
3. APPROVAL:
Approval from Client (wherever applicable)
4. RESPONSIBILITY:
· Contractor has to adhere to all the COVID-19 Government guidelines and must maintain daily records for every labor coming to site. TAPF will not be responsible for any complaintsreportedatsiteduetoanyissueswithlaborarisingforviolatingtheguidelines.

· Contractorwillensurethatanylaborthatcomestositeisprovidedwithcleanmask.

· Quality Engineer will monitor for adherence to COVID-19guidelines.
5. CORONA VIRUS SYMPTOMS CHECK:
Fever (T ≥ 38Celsius), Running Nose, Cough, Sore Throat, Breathing Difficulties, Smell/Taste Loss.

6. ARRANGEMENT OF LOGISTICS MADE TO PROJECT SITES:

Logistic arrangements shall be made by contractor as per the Government guidelines ensuring social distance is maintained.

7. DEMONSTRATION AT PROJECTSITES

[image: image1.jpg]I:HT HEGDE AND HEGDE
ARCHITECTURE * ENGINEERING * INTERIORS

201 MARVEL SIGNET SHIRUR PARK MAIN ROAD VIDYANAGAR HUBBALLI - 580 031
PH: 0836 2374312. email : harch@hegdeandhegde.com

458 FIRST FLOOR 10TH CROSS II-PHASE GIRINAGAR BENGALURU - 560 085
PH: 080 26721672. email : barch@hegdeandhegde.com




TAPF will display contact number of SPOC (Single point of Contact), Posters relating to COVID-19, emergency contact numbers etc.

8. PROCEDURE:

8.1 SECURITY GATE MANAGEMENT:

· Mandatory / Compulsory screening all persons irrespective of cadre / status entering the site non- contact Thermometer.

· Single point entry and exit for all project sites.

· Stoppage of any person into site if found fever and cough with breathing.

· All vehicles including two wheelers shall be parked in designated areas only.

· No new workers shall be allowed inside.

· If anyone leaves and re-enters the site during the shift, re-screening of
 the individual will be done prior to re-entry into the worksite.

8.2 [image: image2.png]


PROVISION OF HANDWASH:

· Hand wash arrangements will be made at entry / exit points.

· Everyone will be required to wash hands for at least 20 seconds with soap, before entering the site and using PPEs. Same procedure to be followed removing PPEs and exiting the premise.
[image: image3.png]ce e
glelalelale

5 o i





8.3 MANDATORY USE OF PPE’S:

· Mandatory use of face mask by everyone entering the premise.
· Re-usable PPEs should be thoroughly cleaned and should not be shared with others.
· Proper disposal of used nose mask while leaving the site.
8.4 [image: image4.png]


SOCIAL DISTANCING:

· Always maintain social distancing (at least 1.5- 2mtr) at project sites, plants, offices, labor camp, rest shed etc.
8.5 RECORD OF WORKERS:

· Contractor has to maintain all the records related to travel history of their workers and self- declaration form. The same record shall be documented and records to shall be updated daily basis at site. The same shall be signed jointly by Contractor supervisor and TAPFQC personnel.
· Any deviation to the procedure / guidelines shall be charged with a penalty of 1000 per person per day.
[image: image5.png]



8.6 EATING:

Food should be consumed at designated areas only ensuring social distancing guidelines.

8.7 [image: image6.png]


CLEANING AND DISINFECTION:

· Contractor should arrange a housekeeping team to spray the disinfectant liquid.

· Entire construction site including site office, Workmen camp, pantry, pathways, toilets, entry/exit gates will be disinfected twice a day by sodium hypochlorite or phenol disinfectants.
9. PRECAUTIONS MEASURE TO BE FOLLOWED:

· On day 1, before resuming the work at site, mandatory medical check to be arranged by contractor for all workers and a health certificate must be submitted.
· The workers coming from outside should have been quarantined for a period of at least 14 days. Only medically fit workers shall be deployed at site.
· Start time on site will best aggered to avoid congestion at the entry gates. Number of workers working at a particular time/place to be reduced by making arrangements for different shifts
/ areas
10. GUIDELINE FOR WORKMENCAMP:

· Proper hygiene to be maintained at labour camp area, special attention to be given to washrooms / toilets by disinfecting, and maintaining dry.
· Arrangements to be made by contractor to restrict movements of laborers.
· All shall be advised to wear mask and awareness to be arranged
· Records to be maintained at worker camp by contractor and verified by Safety in charge.
11. [image: image7.png]


DO’S

· Conduct warm up exercise at site.
· Wash your hands soap and water regularly.
· Wash hands before touching eyes, nose and mouth.
· Covery our nose and mouth with and kerchief/tissue while sneezing and coughing.
12. DON’T

· Don’t come in close contact with anyone.
· Don’t touch your eyes, nose and mouth.
· Don’t spit in Public.
· Avoid workers frequent trips to the market to buy groceries/medical supplies.
Instructions for Hand wash

[image: image8.png]



OFFENCE AND PENALTIES FOR VIOLATION OF LOCKDOWN MEASURES:

· Section 51 to 60 of the Disaster Management Act 2005
· Section 188 in the Indian Penal Code,186
1

